## Outdoor Air
ASHRAE 62.1-2010 OUTDOOR AIR
[6 empty] | Code Area+People |  |  | Code Combined |  | Proposed OA
Zone | Space | Space Function | Area ft² | # of occupants | Occupancy Density occ/ft² | CFM/occ | CFM/ft² | Minimum CFM Required | CFM/occ | Minimum CFM Required | Provided CFM
AHU-1
Zone 1 | Space 1 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 1 | Space 2 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 1 | Space 3 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 1 Eff | Ceiling Supply of Cool Air |  |  | Ez = | 1 |  |  | 81 |  | 90
Zone 2 | Space 4 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 2 | Space 5 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 2 | Space 6 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 2 Eff | Ceiling Supply of Cool Air |  |  | Ez = | 1 |  |  | 81 |  | 90
| Total AHU-1 OA |  | 600 | 18 |  |  |  | 162 |  | 180 | 180
AHU-2
Zone 3 | Space 7 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 3 | Space 8 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 3 | Space 9 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 3 Eff | Ceiling Supply of Cool Air |  |  | Ez = | 1 |  |  | 81 |  | 90
Zone 4 | Space 10 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 4 | Space 11 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 4 | Space 12 | Correctional Facility - Cell | 100 | 3 | 0.025 | 5 | 0.12 | 27 | 10 | 30
Zone 4 Eff | Ceiling Supply of Cool Air |  |  | Ez = | 1 |  |  | 81 |  | 90
| Total AHU-2 OA |  | 600 | 18 |  |  |  | 162 |  | 180 | 180
| Total Building OA | [6 empty] | 324 |  |  | 360
Notes:
1. Residential Dwelling requires 2 occupants for first bedroom and 1 per extra bedrooms

## ASHRAE62.1-2010 (hidden)
(Entered October 13/2010) | People Rate | Area Rate | Density | Density | Combined
Occupancy Category | cfm/person | cfm/ft² | #/1000ft² | person/ft² | cfm/person
Correctional Facility - Cell | 5 | 0.12 | 25 | 0.025 | 10
Correctional Facility - Dayroom | 5 | 0.06 | 30 | 0.03 | 7
Correctional Facility - Guard Stations | 5 | 0.06 | 15 | 0.015 | 9
Correctional Facility - Booking/Waiting | 7.5 | 0.06 | 50 | 0.05 | 9
Educational Facilities - Daycare (through age 4) | 10 | 0.18 | 25 | 0.025 | 17
Educational Facilities - Daycare Sickroom | 10 | 0.18 | 25 | 0.025 | 17
Educational Facilities - Classrooms (ages 5-8) | 10 | 0.12 | 25 | 0.025 | 15
Educational Facilities - Classrooms (age 9 plus) | 10 | 0.12 | 35 | 0.035 | 13
Educational Facilities - Lecture Classroom | 7.5 | 0.06 | 65 | 0.065 | 8
Educational Facilities - Lecture Hall (fixed seats) | 7.5 | 0.06 | 150 | 0.15 | 8
Educational Facilities - Art Classroom | 10 | 0.18 | 20 | 0.02 | 19
Educational Facilities - Science Laboratories | 10 | 0.18 | 25 | 0.025 | 17
Educational Facilities - University/College Laboratories | 10 | 0.18 | 25 | 0.025 | 17
Educational Facilities - Wood/Metal Shop | 10 | 0.18 | 20 | 0.02 | 19
Educational Facilities - Computer Lab | 10 | 0.12 | 25 | 0.025 | 15
Educational Facilities - Media Center | 10 | 0.12 | 25 | 0.025 | 15
Educational Facilities - Music/Theater/Dance | 10 | 0.06 | 35 | 0.035 | 12
Educational Facilities - Multi-use Assembly | 7.5 | 0.06 | 100 | 0.1 | 8
Food and Beverage Service - Restaurant Dining Rooms | 7.5 | 0.18 | 70 | 0.07 | 10
Food and Beverage Service - Cafeteria/Fast-food Dining | 7.5 | 0.18 | 100 | 0.1 | 9
Food and Beverage Service - Bars, Cocktail Lounges | 7.5 | 0.18 | 100 | 0.1 | 9
Food and Beverage Service - Kitchen (Cooking) | 7.5 | 0.12 | 20 | 0.02 | 14
General - Break Rooms | 5 | 0.06 | 25 | 0.025 | 7
General - Coffee Stations | 5 | 0.06 | 20 | 0.02 | 8
General - Conference/Meeting | 5 | 0.06 | 50 | 0.05 | 6
General - Corridors | 0 | 0.06 | 0 | 0 | 0
General - Occupiable Storage Rooms for Liquids or Gels | 5 | 0.12 | 2 | 0.002 | 65
Hotels, Motels, Resorts, Dormitories - Bedroom/Living Rooms | 5 | 0.06 | 10 | 0.01 | 11
Hotels, Motels, Resorts, Dormitories - Barracks Sleeping Areas | 5 | 0.06 | 20 | 0.02 | 8
Hotels, Motels, Resorts, Dormitories - Laundry Rooms, Central | 5 | 0.12 | 10 | 0.01 | 17
Hotels, Motels, Resorts, Dormitories - Laundry Rooms within Dwelling Units | 5 | 0.12 | 10 | 0.01 | 17
Hotels, Motels, Resorts, Dormitories - Lobbies/Prefunction | 7.5 | 0.06 | 30 | 0.03 | 10
Hotels, Motels, Resorts, Dormitories - Multipurpose Assembly | 5 | 0.06 | 120 | 0.12 | 6
Office Buildings - Breakrooms | 5 | 0.12 | 50 | 0.05 | 7
Office Buildings - Main Entry Lobbies | 5 | 0.06 | 10 | 0.01 | 11
Office Buildings - Occupiable Storage Rooms for Dry Materials | 5 | 0.06 | 2 | 0.002 | 35
Office Buildings - Office Space | 5 | 0.06 | 5 | 0.005 | 17
Office Buildings - Reception Areas | 5 | 0.06 | 30 | 0.03 | 7
Office Buildings - Telephone/Data Entry | 5 | 0.06 | 60 | 0.06 | 6
Miscellaneous Spaces - Bank Vaults/Safe Deposit | 5 | 0.06 | 5 | 0.005 | 17
Miscellaneous Spaces - Banks or Bank Lobbies | 7.5 | 0.06 | 15 | 0.015 | 12
Miscellaneous Spaces - Computer (Not Printing) | 5 | 0.06 | 4 | 0.004 | 20
Miscellaneous Spaces - General Manufacturing | 10 | 0.18 | 7 | 0.007 | 36
Miscellaneous Spaces - Pharmacy (Prep. Area) | 5 | 0.18 | 10 | 0.01 | 23
Miscellaneous Spaces - Photo Studios | 5 | 0.12 | 10 | 0.01 | 17
Miscellaneous Spaces - Shipping/Receiving | 10 | 0.12 | 2 | 0.002 | 70
Miscellaneous Spaces - Sorting, Packing, Light Assembly | 7.5 | 0.12 | 7 | 0.007 | 25
Miscellaneous Spaces - Telephone Closets | 0 | 0 | 0 | 0 | 0
Miscellaneous Spaces - Transportation Waiting | 7.5 | 0.06 | 100 | 0.1 | 8
Miscellaneous Spaces - Warehouses | 10 | 0.06 | 0 | 0 | 0
Public Assembly Spaces - Auditorium Seating Area | 5 | 0.06 | 150 | 0.15 | 5
Public Assembly Spaces - Places of Religious Worship | 5 | 0.06 | 120 | 0.12 | 6
Public Assembly Spaces - Courtrooms | 5 | 0.06 | 70 | 0.07 | 6
Public Assembly Spaces - Legislative Chambers | 5 | 0.06 | 50 | 0.05 | 6
Public Assembly Spaces - Libraries | 5 | 0.12 | 10 | 0.01 | 17
Public Assembly Spaces - Lobbies | 5 | 0.06 | 150 | 0.15 | 5
Public Assembly Spaces - Museums (Children's) | 7.5 | 0.12 | 40 | 0.04 | 11
Public Assembly Spaces - Museums/Galleries | 7.5 | 0.06 | 40 | 0.04 | 9
Residential - Dwelling Unit | 5 | 0.06 | 0 | 0 | 0
Residential - Common Corridors | 0 | 0.06 | 0 | 0 | 0
Retail - Sales (Except as Below) | 7.5 | 0.12 | 15 | 0.015 | 16
Retail - Mall Common Areas | 7.5 | 0.06 | 40 | 0.04 | 9
Retail - Barbershop | 7.5 | 0.06 | 25 | 0.025 | 10
Retail - Beauty and Nail Salons | 20 | 0.12 | 25 | 0.025 | 25
Retail - Pet Shops (Animal Areas) | 7.5 | 0.18 | 10 | 0.01 | 26
Retail - Supermarket | 7.5 | 0.06 | 8 | 0.008 | 15
Retail - Coin-operated Laundries | 7.5 | 0.12 | 20 | 0.02 | 14
Sports and Entertainment - Sports Arena (Play Area) | 0 | 0.3 | 0 | 0 | 0
Sports and Entertainment - Gym, Stadium (Play Area) | 0 | 0.3 | 30 | 0.03 | 0
Sports and Entertainment - Spectator Areas | 7.5 | 0.06 | 150 | 0.15 | 8
Sports and Entertainment - Swimming (Pool & Deck) | 0 | 0.48 | 0 | 0 | 0
Sports and Entertainment - Disco/Dance Floors | 20 | 0.06 | 100 | 0.1 | 21
Sports and Entertainment - Health Club/Aerobics Room | 20 | 0.06 | 40 | 0.04 | 22
Sports and Entertainment - Health Club/Weight Rooms | 20 | 0.06 | 10 | 0.01 | 26
Sports and Entertainment - Bowling Alley (Seating) | 10 | 0.12 | 40 | 0.04 | 13
Sports and Entertainment - Gambling Casinos | 7.5 | 0.18 | 120 | 0.12 | 9
Sports and Entertainment - Game Arcades | 7.5 | 0.18 | 20 | 0.02 | 17
Sports and Entertainment - Stages, Studios | 10 | 0.06 | 70 | 0.07 | 11
Copyright MMM Group Ltd. - by Omid M.

## Eff (hidden)
Config | Effectiveness
Ceiling Supply of Cool Air | 1
Ceiling Supply of Warm Air and Floor Return | 1
Ceiling Supply of Warm Air 15°F or more above Space Temperature and Ceiling Return | 0.8
Ceiling Supply of Warm Air Less Than 15°F Above Space Temperature and Ceiling Return (See 62.1) | 1
Floor Supply of Cool Air and Ceiling Return Provided that the 150fpm Supply Jet Reaches 4.5ft Above the Floor | 1
Floor Supply of Cool Air and Ceiling Return, Provided Low-velocity Displacement Ventilation (See 62.1) | 1.2
Floor Supply of Warm Air and Floor Return | 1
Floor Supply of Warm Air and Ceiling Return | 0.7
Makeup Supply Drawn in on the Opposite Side of the Room from the Exhaust and/or Return | 0.8
Makeup Supply Drawn in Near to the Exhaust and/or Return Location | 0.5