## page 1 of 5
Meter Sizing Worksheet
Project & Owner Information
Project Name
Project Address
Project Lot & Square
Owner’s Name
Owner’s Address
Owner’s phone or email
Designer Information
Designer’s Name
Designer’s Company
Designer’s Address
Designer’s phone and/or email
Type of Occupancy
Hotel____Shopping Center____Restaurant____School____Public Building____Office____ Mixed Use____
Hospital____Apartment____Condominiums____Commercial____ Single Family Home____
Hydrant Flow Test Results
Static Pressure:______ Residual Pressure:______
A hydrant flow test is required for a water connection 3" diameter and larger. If your connection is 2" and smaller assume a working pressure at meter discharge of 60 psi and a pressure adjustment factor of 1.0. See page 2 of 5.
Indoor Fire Detector Check Installation?
No____Yes____ Designer has confirmed that the drainage system has the capacity to handle flow test.
Agreement and Signature
The designer is responsible for determining required domestic, irrigation, mechanical, and fire flows in addition to the proper sizing of meters. By submitting this application, I affirm that the information provided is correct.
Designer’s Name (printed)
Signature/Date
DC Water Use Only
The information provided in this application has been reviewed and approved.
Tracking No: Reviewer Date

## page 2 of 5
Project Name: | 0
Domestic Demand (Continuous)
Fixture Type (standardized at 60 psi) | Fixture value (gpm) |  | Number of Fixtures |  | Total Fixture Value (gpm)
Bathtub | 8 | x |  | = | 0
Bedpan Washers | 10 | x |  | = | 0
Bidet | 2 | x |  | = | 0
Dental Unit | 2 | x |  | = | 0
Drinking Fountain (public) | 2 | x |  | = | 0
Faucet (kitchen sink) | 2.2 | x |  | = | 0
Faucet (lavatory) | 1.5 | x | 6 | = | 9
Shower Head (shower only) | 2.5 | x |  | = | 0
Faucet (utility sink) | 4 | x | 3 | = | 12
Urinal (flush valve) | 35 | x |  | = | 0
Urinal (wall or stall) | 16 | x |  | = | 0
Urinal Trough (2 ft. unit) | 2 | x |  | = | 0
Toilet Flush Valve | 35 | x |  | = | 0
Toilet Tank Type | 4 | x | 6 | = | 24
Dishwasher | 2 | x | 1 | = | 2
Clothes Washer | 6 | x |  | = | 0
Hose (50 ft length wash down) 1/2" connection | 5 | x |  | = | 0
Hose (50 ft length wash down) 5/8" connection | 9 | x |  | = | 0
Hose (50 ft length wash down) 3/4" connection | 12 | x | 5 | = | 60
other |  | x |  | = | 0
Total Fixture Value |  |  |  | = | 107
Water Flow Demand per fixture value (Figures 1 & 2 (see page 5 of 5)) gpm |  |  |  | = | 51
Pressure adjustment factor (Table 1 (see page 4 of 5)) |  |  |  | = | 1.17
Water Flow Demand x Pressure Factor gpm |  |  |  | = | 59.67
Total Domestic Demand gpm |  |  |  | = | 59.67
Information obtained from the American Water Works Association M22 2nd Ed.

## page 3 of 5
|  |  | Project Name: | 0
Irrigation Demand (Intermittent)
| 100 Sq. Ft. |  | Factor |  | Fixture Value (gpm)
Irrigated Area with SPRAY Systems | 25 | x | 1.16 | = | 29
Irrigated Area with ROTARY Systems |  | x | 0.4 | = | 0
Number of Hose Bibs |  | x | 6.5 | = | 0
Sub-Total Irrigation Demand (Irrigation + Hose Bib) gpm |  |  |  | = | 29
Pressure adjustment factor (Table 1 (see page 4 of 5)) |  |  |  | = | 1.09
Sub-Total Irrigation Demand x Pressure Factor gpm |  |  |  | = | 31.61
Total Fixed Demands (if any) gpm |  |  |  | = | 0
Total Irrigation Demand gpm |  |  |  | = | 34
Mechanical Demand (Continuous and/or Intermittent)
Total Continuous Mechanical Demand* gpm |  |  |  | = | 0
Total Intermittent Mechanical Demand* gpm |  |  |  | =
*Mechanical water demand refers to the intermittent and/or continuous operation of process equipment, cooling towers, A/C systems, wash down systems, etc. It is the responsibility of the MEP to determine those demand values based on type of equipment and usage.
Fire Demand, if required by code (Intermittent)
Does the building require a fire pump? |  |  | yes | x | no
Actual Fire Flow Demand (Per NFPA requirements) gpm |  |  |  | = | 0
Pump Test Demand (if required, 150% of actual demand) gpm |  |  |  | = | 0
Fire Service Lateral Sizing
Fire Service Lateral Size (in) |  |  |  | =
See Table 4 on page 4 of 5. The velocity in the lateral must be ≤ 15 fps.
Meter Selection**
Combined Meter Size (in)______Domestic Meter Size(in)______
**You will have either a large (3" or more) separate domestic and fire services Or a small (2" or less) combined service
Acceptance Criteria Verification (refer to Tables 2 & 3 on page 4 of 5)
Dedicated Domestic Service Only
Normal Operating Demand = Domestic + Mechanical (cont.) gpm | 59.67 | ≤ | _____ gpm |  | Is the flow rate within the Max Rate for Cont. Operation?
Total Flow Thru Meter = Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.) gpm | 93.67 | ≤ | 48 |  | Is the flow rate within Safe Max Operating Capacity?
Combined Domestic & Fire Service (for 2" and small services)
Total flow through meter = Domestic+Irrigation+Mechanical(cont.+ inter)+Fire | 93.67 | ≤ | _____ gpm |  | Is the flow rate within Safe Max Operating Capacity?
If your meter is sized smaller or larger than recommended please provide an explanation.

## page 4 of 5
Table 1 Pressure adjustment factors (60 psi)
Working Pressure at Meter Discharge (psi) | Pressure Adjustment Factor
35 | 0.74
40 | 0.8
50 | 0.9
60 | 1
70 | 1.09
80 | 1.17
90 | 1.25
100 | 1.34
1. Copyright 2004 American Water Works Association Sizing Water Service Lines and Meters M22, All Rights Reserved.
2. Working pressure at meter discharge = Static pressure in the main. Information is obtained from a fire hydrant flow test.
3. A hydrant flow test is required for a water connection 3" diameter and larger. If your connection is 2" and smaller assume a working pressure at meter discharge of 60 psi and a pressure adjustment factor of 1.0. See page 2 of 5.
Table 2 Cold-Water Meters - Displacement Type, Bronze Main Case
Meter Size | Low Flow Registration | Normal Operating Range | Recommended Max Rate for Continuous Operations | Safe Max Operating Capacity
1-inch | 3/4 gpm | 3-50 gpm | 25 gpm | 50 gpm
1 1/2 inch | 1 1/2 gpm | 5-100 gpm | 50 gpm | 100 gpm
2-inch | 2 gpm | 8-160 gpm | 80 gpm | 160 gpm
Copyright 2003 American Water Works Association C700-02, All Rights Reserved.
Table 3 Cold-Water Meters - Turbine Type, for Customer Service
Meter Size | Low Flow Registration | Normal Operating Range | Recommended Max Rate for Continuous Operations | Safe Max Operating Capacity
3-inch | - | 8-435 gpm | 350 gpm | 435 gpm
4-inch | - | 15-750 gpm | 650 gpm | 750 gpm
6-inch | - | 30-1,600 gpm | 1,400 gpm | 1,600 gpm
8-inch | - | 50-2,800 gpm | 2,400 gpm | 2,800 gpm
10-inch | - | 75-4,200 gpm | 3,500 gpm | 4,200 gpm
12-inch | - | 120-5,300 gpm | 4,400 gpm | 5,300 gpm
Copyright 2007 American Water Works Association C701-07, All Rights Reserved.
Table 4 Fire Service Lateral Velocity Check
Fire Service Lateral Diameter (in) | Fire Service Lateral Area (sf) | Flow Rate thru Fire Lateral* (gpm) | Flow Rate thru Fire Lateral (cfs) | V (fps) = Q (cfs)/A (sf)
2" diameter | 0.021893 | 350 | 0.77 | 35.1713
3" diameter | 0.049063 | 350 | 0.77 | 15.6943
4" diameter | 0.087048 | 350 | 0.77 | 8.8457
6" diameter | 0.19625 | 350 | 0.77 | 3.9236
8" diameter | 0.34924 | 350 | 0.77 | 2.2048
10" diameter | 0.5447 | 350 | 0.77 | 1.4136
12" diameter | 0.785 | 350 | 0.77 | 0.98089
*If NO fire pump is required - enter the actual fire flow demand per NFPA requirements in this entire column. If a fire pump IS required - enter the pump test demand in this column. The pipe size that returns a velocity less than 15 fps is the target pipe size for the fire service.

## page 5 of 5
Figure 1: Water Flow Demand per Fixture Value – Low Range
Figure 2: Water Flow Demand per Fixture Value – High Range