{"text_format":"1","workbook":"xlsx","n_sheets":9,"sheets":["board room","staff and taste","Window","Summary","Solar","Weather_Stations","Wall_R_value","WindowData","RoofData"],"not_rendered":{"charts":2,"images":13,"macros":1,"external_links":1,"defined_names":21,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"board room","index":0,"n_rows":78,"n_cols":15,"rows_kept":78,"cut":false,"hidden":false,"merged":[[25,0,25,5],[25,6,25,11],[25,12,25,17],[50,0,50,5]]}
["PROJECT NUMBER","x1610"]
["PROJECT NAME","16060 westminster"]
["INPUT BY","XT",null,null,"Newfoundland"]
["DATE","2016-12-03"]
["City","North Vancouver",null,{"$f":"VLOOKUP(B5,WeatherData,2,FALSE )","v":"BC"}]
["Latitude",{"$f":"VLOOKUP(B5,WeatherData,23,FALSE )","v":49.32},"N","Lfactor",{"$f":"1+(B6-40)*0.0375","v":1.3494999999999999}]
["Winter Design Temp.",{"$f":"D7","v":-7},"degC",{"$f":"VLOOKUP(B5,WeatherData,4,FALSE )","v":-7}]
["Summer Design Temp",{"$f":"D8","v":26},"degC",{"$f":"VLOOKUP(B5,WeatherData,5,FALSE )","v":26}]
["Wall Type","Wall Type 3"]
["Wall R value",{"$f":"D10*0.176","v":2.6399999999999997},"m2/oC/Watt",{"$f":"VLOOKUP(B9,Wall_R_value!B2:D13,2,FALSE)","v":15},"R-Value"]
["Window Type","Window Type 2"]
["Window R value",{"$f":"D12*0.175","v":0.35},"m2/oC/Watt",{"$f":"VLOOKUP(B11,WindowData,3,FALSE)","v":2},"R-Value","SHGC",0.33]
["Roof Type","Roof Type 6"]
["Roof R Value",{"$f":"D14*0.175","v":5.25},"m2/oC/Watt",{"$f":"VLOOKUP(B13,RoofData,2,FALSE)","v":30},"R-Value"]
["Floor Height",3,"meter"]
["Room temp _Winter",22,"degC"]
["Room Temp_Summer",24,"degC"]
[]
["Heating / Cooling Load Calculation"]
[]
["ROOM NO.",null,"Kitchen"]
[null,null,"Winter",null,"Summer"]
["Room Temperature",null,22,"degC",{"$f":"$B$17","v":24},"degC"]
["Temperature difference",null,{"$f":"OT-RoomT","v":-29},"degC",{"$f":"OT_Summer-E23","v":2},"degC"]
["Envelope-Wall"]
["Wall 1",null,null,null,null,null,"Wall 2"]
["Wall dimension","Length",9.0909090909090917,"m",12,"ft","Wall dimension","Length",13.333333333333334,"m",27,"ft"]
[null,"Height",3.0303030303030303,"m",10,"ft",null,"Height",3.0303030303030303,"m",10,"ft"]
[null,"Area",27.548209366391188,"m2",300,"sqft",null,"Area",40.404040404040408,"m2",440,"sqft"]
["Wall R Value","R value",2.625,"m2/oC/Watt",15,"R-Value","Wall R Value","R value",2.625,"m2/oC/Watt",15,"R-Value"]
[null,"U value",0.38095238095238093,"Watt/m2/oC",6.6666666666666666E-2,"1/R",null,"U value",0.38095238095238093,"Watt/m2/oC",6.6666666666666666E-2,"1/R"]
["Wall Direction","Angle",0,"Degree",null,null,"Wall Direction","Angle",90,"Degree"]
["Window dimension","Length",1.5151515151515151,"m",10,"ft","Window dimension","Length",2.4242424242424243,"m",0,"ft"]
[null,"Height",1.2121212121212122,"m",5,"ft",null,"Height",1.2121212121212122,"m",0,"ft"]
[null,"Amount",4,"#",1,"#",null,"Amount",3,"#",0,"#"]
[null,"Area",7.3461891643709825,"m2",80,"sqft",null,"Area",8.8154269972451793,"m2",96,"sqft"]
["Window Thermal","R value",0.4375,"m2/oC/Watt",2.5,"R-Value","Window Thermal","R value",0.4375,"m2/oC/Watt",2.5,"R-Value"]
[null,"U value",2.2857142857142856,"Watt/m2/oC",0.4,"1/R",null,"U value",2.2857142857142856,"Watt/m2/oC",0.4,"1/R"]
[null,"SHGC",0.65,null,null,null,null,"SHGC",0.65]
[null,"Solar0",93,"watt/m2",null,null,null,"Solar0",285,"watt/m2"]
[null,"SolarCorrect",-6.7,"degC",null,null,null,"SolarCorrect",-1.1000000000000001,"degC"]
[null,"Shading Factor",0.5,null,null,null,null,"Shading Factor",0.5]
["Act. Wall ","Area",20.202020202020204,"m2",null,null,"Act. Wall ","Area",31.588613406795229,"m2"]
["Heating",null,null,null,null,null,"Heating"]
["Wall Heat Loss",null,{"$f":"C31*C43*(OT-RoomT)","v":-223.18422318422321},"watt",{"$f":"2.3*3*(1/2.1)*(22+30)","v":170.85714285714283},null,"Wall Heat Loss",null,{"$f":"I31*I43*(OT-RoomT)","v":-348.97896716078537},"watt"]
["Window Heat Loss",null,{"$f":"C36*C38*(OT-RoomT)","v":-486.9473960383051},"watt",null,null,"Window Heat Loss",null,{"$f":"I36*I38*(OT-RoomT)","v":-584.3368752459661},"watt"]
["Cooling",null,null,null,null,null,"Cooling"]
["Wall Heat Gain",null,{"$f":"C43*C31*($E$24+C41)","v":-36.171236171236174},"watt",null,null,"Wall Heat Gain",null,{"$f":"I43*I31*($E$24-I41)","v":37.304648213739128},"watt"]
["Window Heat Gain",null,{"$f":"C36*C39*C40+C36*C38*$E$24","v":477.65971402335038},"watt",null,null,"Window Heat Gain",null,{"$f":"I36*I39*I40+I36*I38*$E$24","v":1673.3569460842189},"watt"]
["Envelope-Roof",null,null,null,null,null,"Ventilation "]
["Roof",null,null,null,null,null,"HRV effectiveness",null,0]
["Roof dimension","Length",{"$f":"E52/3.3","v":3.6363636363636367},"m",12,"ft","Venting Rate",null,{"$f":"K52/2.12","v":18.867924528301884},"L/s",40,"CFM"]
[null,"Width",9.0909090909090917,"m",27,"ft","Venting Heating",null,{"$f":"I52*1.2*C24*(1-I51)","v":-656.60377358490553},"watt"]
[null,"Area",{"$f":"C53*C52","v":33.057851239669425},"m2",null,null,"Venting Cooling",null,{"$f":"I52*1.2*E24*(1-I51)","v":45.283018867924518},"watt"]
["Roof R Value","R value",{"$f":"E55*0.175","v":5.25},"m2/oC/Watt",{"$f":"$D$14","v":30},"R-Value","Volumn",{"$f":"B78*B15","v":99.173553719008282},"m3"]
[null,"U value",{"$f":"1/C55","v":0.19047619047619047},"Watt/m2/oC",{"$f":"1/E55","v":3.3333333333333333E-2},"1/R","Air Change",{"$f":"I52*3600/1000/H55","v":0.68490566037735823},"per Hr"]
[null,"Angle","Flat","Degree",null,null,"People"]
["Sky Light dimension","Length",0,"m",null,null,"Person Amount",10,"#",164,"watt per Person"]
[null,"Height",0,"m",null,null,"People heat",{"$f":"J58*H58","v":1640},"watt"]
[null,"Amount",0,"#",null,null,"Lighting"]
[null,"Area",{"$f":"C58*C59*C60","v":0},"m2",null,null,"Light Density",1.5,"w/m2"]
["Window Thermal","R value",{"$f":"E62*0.175","v":0.35},"m2/oC/Watt",{"$f":"$D$12","v":2},"R-Value","Light heat",{"$f":"H61*B78","v":49.586776859504141},"watt"]
[null,"U value",{"$f":"1/C62","v":2.8571428571428572},"Watt/m2/oC",{"$f":"1/E62","v":0.5},"1/R"]
[null,"SHGC",{"$f":"$G$12","v":0.33}]
[null,"Solar0",{"$f":"VLOOKUP(C57,[0]!SolarCorrection,2, FALSE)","v":534},"watt/m2"]
[null,"SolarCorrect",{"$f":"VLOOKUP(C57,[0]!SolarCorrection,4, FALSE)","v":-6.1},"degC",null,null,null,null,null,null,null,null,"Wall",{"$f":"C45+I45","v":-572.16319034500862},{"$f":"N66/$N$70","v":0.23046409695960407}]
[null,"Shading Factor",0.5,null,null,null,null,null,null,null,null,null,"Window",{"$f":"C46+I46","v":-1071.2842712842712},{"$f":"N67/$N$70","v":0.43150724537117346}]
["Act. Wall ","Area",{"$f":"C54-C61","v":33.057851239669425},"m2",null,null,null,null,null,null,null,null,"Roof",{"$f":"C70","v":-182.60527351436443},{"$f":"N68/$N$70","v":7.3552371370086397E-2}]
["Heating",null,null,null,null,null,null,null,null,null,null,null,"Vent",{"$f":"I53","v":-656.60377358490553},{"$f":"N69/$N$70","v":0.26447628629913605}]
["Roof Heat Loss",null,{"$f":"C56*C68*(OT-RoomT)","v":-182.60527351436443},"watt",null,null,null,null,null,null,null,null,"Total",{"$f":"SUM(N66:N69)","v":-2482.6565087285499},{"$f":"N70/$N$70","v":1}]
["Skylight Heat Loss",null,{"$f":"C61*C63*(OT-RoomT)","v":0},"watt"]
["Cooling"]
["Roof Heat Gain",null,{"$f":"C68*C56*($E$24+C66)","v":-25.816607634789452},"watt"]
["Skylight Heat Gain",null,{"$f":"C61*C64*C65+C61*C63*$E$24","v":0},"watt"]
[]
["Room Heating Load",{"$f":"C70+I45+C45+I46+C46+I53+O45+O46","v":-2482.6565087285499}," watt","Room Cooling Load",null,{"$f":"C48+C49+I48+I49+C73+C74+I54+H59+H62+O45+O46","v":3861.2032602427116}," watt"]
["Eningeering check",{"$f":"B76/B78","v":-75.10035938903863},"watt/m2","Eningeering check",null,{"$f":"F76/B78","v":116.80139862234202},"watt/m2"]
["Room Area",{"$f":"C52*C53","v":33.057851239669425},"m2"]

{"sheet":"staff and taste","index":1,"n_rows":78,"n_cols":18,"rows_kept":78,"cut":false,"hidden":false,"merged":[[25,12,25,17],[50,0,50,5],[25,0,25,5],[25,6,25,11]]}
["PROJECT NUMBER","x1610"]
["PROJECT NAME","16060 westminster"]
["INPUT BY","XT",null,null,"Manitoba"]
["DATE","2016-12-03"]
["City","Richmond",null,{"$f":"VLOOKUP(B5,WeatherData,2,FALSE )","v":"BC"}]
["Latitude",{"$f":"VLOOKUP(B5,WeatherData,23,FALSE )","v":49.17},"N","Lfactor",{"$f":"1+(B6-40)*0.0375","v":1.3438750000000002}]
["Winter Design Temp.",-10,"degC"]
["Summer Design Temp",30,"degC"]
["Wall Type","Wall Type 3"]
["Wall R value",{"$f":"D10*0.176","v":2.6399999999999997},"m2/oC/Watt",{"$f":"VLOOKUP(B9,Wall_R_value!B2:D13,2,FALSE)","v":15},"R-Value"]
["Window Type","Window Type 2"]
["Window R value",{"$f":"D12*0.175","v":0.35},"m2/oC/Watt",{"$f":"VLOOKUP(B11,WindowData,3,FALSE)","v":2},"R-Value","SHGC",0.33]
["Roof Type","Roof Type 6"]
["Roof R Value",{"$f":"D14*0.175","v":5.25},"m2/oC/Watt",{"$f":"VLOOKUP(B13,RoofData,2,FALSE)","v":30},"R-Value"]
["Floor Height",3,"meter"]
["Room temp _Winter",22,"degC"]
["Room Temp_Summer",24,"degC"]
[]
["Heating / Cooling Load Calculation"]
[]
["ROOM NO.",null,"Kitchen"]
[null,null,"Winter",null,"Summer"]
["Room Temperature",null,22,"degC",{"$f":"$B$17","v":24},"degC"]
["Temperature difference",null,{"$f":"OT-RoomT","v":-32},"degC",{"$f":"OT_Summer-E23","v":6},"degC"]
["Envelope-Wall"]
["Wall 1",null,null,null,null,null,"Wall 2",null,null,null,null,null,"Wall 3"]
["Wall dimension","Length",9.0909090909090917,"m",30,"ft","Wall dimension","Length",13.333333333333334,"m",44,"ft","Wall dimension","Length",9.0909090909090917,"m",30,"ft"]
[null,"Height",3.0303030303030303,"m",10,"ft",null,"Height",3.0303030303030303,"m",10,"ft",null,"Height",3.0303030303030303,"m",10,"ft"]
[null,"Area",27.548209366391188,"m2",300,"sqft",null,"Area",40.404040404040408,"m2",440,"sqft",null,"Area",27.548209366391188,"m2",300,"sqft"]
["Wall R Value","R value",2.625,"m2/oC/Watt",15,"R-Value","Wall R Value","R value",2.625,"m2/oC/Watt",15,"R-Value","Wall R Value","R value",2.625,"m2/oC/Watt",15,"R-Value"]
[null,"U value",0.38095238095238093,"Watt/m2/oC",6.6666666666666666E-2,"1/R",null,"U value",0.38095238095238093,"Watt/m2/oC",6.6666666666666666E-2,"1/R",null,"U value",0.38095238095238093,"Watt/m2/oC",6.6666666666666666E-2,"1/R"]
["Wall Direction","Angle",0,"Degree",null,null,"Wall Direction","Angle",90,"Degree",null,null,"Wall Direction","Angle",270,"Degree"]
["Window dimension","Length",1.5151515151515151,"m",5,"ft","Window dimension","Length",2.4242424242424243,"m",8,"ft","Window dimension","Length",2.4242424242424243,"m",8,"ft"]
[null,"Height",1.2121212121212122,"m",4,"ft",null,"Height",1.2121212121212122,"m",4,"ft",null,"Height",1.5151515151515151,"m",5,"ft"]
[null,"Amount",4,"#",4,"#",null,"Amount",3,"#",3,"#",null,"Amount",2.5,"#",2.5,"#"]
[null,"Area",7.3461891643709825,"m2",80,"sqft",null,"Area",8.8154269972451793,"m2",96,"sqft",null,"Area",9.1827364554637274,"m2",100,"sqft"]
["Window Thermal","R value",0.4375,"m2/oC/Watt",2.5,"R-Value","Window Thermal","R value",0.4375,"m2/oC/Watt",2.5,"R-Value","Window Thermal","R value",0.4375,"m2/oC/Watt",2.5,"R-Value"]
[null,"U value",2.2857142857142856,"Watt/m2/oC",0.4,"1/R",null,"U value",2.2857142857142856,"Watt/m2/oC",0.4,"1/R",null,"U value",2.2857142857142856,"Watt/m2/oC",0.4,"1/R"]
[null,"SHGC",0.65,null,null,null,null,"SHGC",0.65,null,null,null,null,"SHGC",0.65]
[null,"Solar0",93,"watt/m2",null,null,null,"Solar0",285,"watt/m2",null,null,null,"Solar0",285,"watt/m2"]
[null,"SolarCorrect",-6.7,"degC",null,null,null,"SolarCorrect",-1.1000000000000001,"degC",null,null,null,"SolarCorrect",-1.1000000000000001,"degC"]
[null,"Shading Factor",0.5,null,null,null,null,"Shading Factor",0.5,null,null,null,null,"Shading Factor",0.5]
["Act. Wall ","Area",20.202020202020204,"m2",null,null,"Act. Wall ","Area",31.588613406795229,"m2",null,null,"Act. Wall ","Area",18.365472910927458,"m2"]
["Heating",null,null,null,null,null,"Heating",null,null,null,null,null,"Heating"]
["Wall Heat Loss",null,{"$f":"C31*C43*(OT-RoomT)","v":-246.27224627224629},"watt",{"$f":"2.3*3*(1/2.1)*(22+30)","v":170.85714285714283},null,"Wall Heat Loss",null,{"$f":"I31*I43*(OT-RoomT)","v":-385.08023962569422},"watt",null,null,"Wall Heat Loss",null,-209.89111898202808,"watt"]
["Window Heat Loss",null,{"$f":"C36*C38*(OT-RoomT)","v":-537.32126459399183},"watt",null,null,"Window Heat Loss",null,{"$f":"I36*I38*(OT-RoomT)","v":-644.78551751279019},"watt",null,null,"Window Heat Loss",null,-629.67335694608414,"watt"]
["Cooling",null,null,null,null,null,"Cooling",null,null,null,null,null,"Cooling"]
["Wall Heat Gain",null,{"$f":"C43*C31*($E$24+C41)","v":-5.3872053872053893},"watt",null,null,"Wall Heat Gain",null,{"$f":"I43*I31*($E$24-I41)","v":85.439678166950898},"watt",null,null,"Wall Heat Gain",null,48.274957365866463,"watt"]
["Window Heat Gain",null,{"$f":"C36*C39*C40+C36*C38*$E$24","v":544.82487209759938},"watt",null,null,"Window Heat Gain",null,{"$f":"I36*I39*I40+I36*I38*$E$24","v":1753.9551357733176},"watt",null,null,"Window Heat Gain",null,1869.0148235602778,"watt"]
["Envelope-Roof",null,null,null,null,null,"Ventilation "]
["Roof",null,null,null,null,null,"HRV effectiveness",null,0]
["Roof dimension","Length",{"$f":"E52/3.3","v":13.333333333333334},"m",44,"ft","Venting Rate",null,{"$f":"K52/2.12","v":47.169811320754718},"L/s",100,"CFM"]
[null,"Width",{"$f":"E53/3.3","v":9.0909090909090917},"m",30,"ft","Venting Heating",null,{"$f":"I52*1.2*C24*(1-I51)","v":-1811.3207547169811},"watt"]
[null,"Area",{"$f":"C53*C52","v":121.21212121212123},"m2",null,null,"Venting Cooling",null,{"$f":"I52*1.2*E24*(1-I51)","v":339.62264150943395},"watt"]
["Roof R Value","R value",{"$f":"E55*0.175","v":5.25},"m2/oC/Watt",{"$f":"$D$14","v":30},"R-Value","Volumn",{"$f":"B78*B15","v":363.63636363636368},"m3"]
[null,"U value",{"$f":"1/C55","v":0.19047619047619047},"Watt/m2/oC",{"$f":"1/E55","v":3.3333333333333333E-2},"1/R","Air Change",{"$f":"I52*3600/1000/H55","v":0.46698113207547159},"per Hr"]
[null,"Angle","Flat","Degree",null,null,"People"]
["Sky Light dimension","Length",0,"m",null,null,"Person Amount",30,"#",164,"watt per Person"]
[null,"Height",0,"m",null,null,"People heat",{"$f":"J58*H58","v":4920},"watt"]
[null,"Amount",0,"#",null,null,"Lighting"]
[null,"Area",{"$f":"C58*C59*C60","v":0},"m2",null,null,"Light Density",1.5,"w/m2"]
["Window Thermal","R value",{"$f":"E62*0.175","v":0.35},"m2/oC/Watt",{"$f":"$D$12","v":2},"R-Value","Light heat",{"$f":"H61*B78","v":181.81818181818184},"watt"]
[null,"U value",{"$f":"1/C62","v":2.8571428571428572},"Watt/m2/oC",{"$f":"1/E62","v":0.5},"1/R"]
[null,"SHGC",{"$f":"$G$12","v":0.33}]
[null,"Solar0",{"$f":"VLOOKUP(C57,[0]!SolarCorrection,2, FALSE)","v":534},"watt/m2"]
[null,"SolarCorrect",{"$f":"VLOOKUP(C57,[0]!SolarCorrection,4, FALSE)","v":-6.1},"degC",null,null,null,null,null,null,null,null,"Wall",{"$f":"C45+I45","v":-631.35248589794048},{"$f":"N66/$N$70","v":0.14468625778229541}]
[null,"Shading Factor",0.5,null,null,null,null,null,null,null,null,null,"Window",{"$f":"C46+I46","v":-1182.106782106782},{"$f":"N67/$N$70","v":0.27090192946472325}]
["Act. Wall ","Area",{"$f":"C54-C61","v":121.21212121212123},"m2",null,null,null,null,null,null,null,null,"Roof",{"$f":"C70","v":-738.81673881673885},{"$f":"N68/$N$70","v":0.16931370591545206}]
["Heating",null,null,null,null,null,null,null,null,null,null,null,"Vent",{"$f":"I53","v":-1811.3207547169811},{"$f":"N69/$N$70","v":0.41509810683752929}]
["Roof Heat Loss",null,{"$f":"C56*C68*(OT-RoomT)","v":-738.81673881673885},"watt",null,null,null,null,null,null,null,null,"Total",{"$f":"SUM(N66:N69)","v":-4363.5967615384425},{"$f":"N70/$N$70","v":1}]
["Skylight Heat Loss",null,{"$f":"C61*C63*(OT-RoomT)","v":0},"watt"]
["Cooling"]
["Roof Heat Gain",null,{"$f":"C68*C56*($E$24+C66)","v":-2.3088023088023006},"watt"]
["Skylight Heat Gain",null,{"$f":"C61*C64*C65+C61*C63*$E$24","v":0},"watt"]
[]
["Room Heating Load",{"$f":"C70+I45+C45+I46+C46+I53+O45+O46","v":-5203.1612374665547}," watt","Room Cooling Load",null,{"$f":"C48+C49+I48+I49+C73+C74+I54+H59+H62+O45+O46","v":6978.4000257413636}," watt"]
["Eningeering check",{"$f":"B76/B78","v":-42.926080209099069},"watt/m2","Eningeering check",null,{"$f":"F76/B78","v":57.571800212366242},"watt/m2"]
["Room Area",{"$f":"C52*C53","v":121.21212121212123},"m2"]

{"sheet":"Window","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Summary","index":3,"n_rows":32,"n_cols":7,"rows_kept":32,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,1.5]
[null,null,null,null,null,null,1.25]
[null,null,null,null,null,null,1]
[null,null,null,null,null,null,1.25]
[null,null,null,null,null,null,0.5]
[null,null,null,null,null,null,0.25]
[null,null,null,null,null,null,1.5]
[null,null,null,null,null,null,1.5]
[null,null,null,null,null,null,1.25]
[null,null,null,null,null,null,1]
[null,null,null,null,null,null,1.25]
[null,null,null,null,null,null,0.5]
[null,null,null,null,null,null,0.25]
[null,null,null,null,null,null,1.5]
[null,null,null,null,null,"sum",{"$f":"SUM(G17:G30)","v":14.5}]
[null,null,null,null,null,null,{"$f":"G31*1000/20/7","v":103.57142857142857}]

{"sheet":"Solar","index":4,"n_rows":57,"n_cols":6,"rows_kept":57,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,"Solar gain","Solar corrections"]
[null,null,"degree","watt/m2","below 14 C","over 14 C"]
[null,"North",0,93,-3.8,-6.7]
[null,"Northeast",45,194,-0.6,-3.3]
[null,"East",90,285,1.7,-1.1000000000000001]
[null,"Southeast",135,252,0.6,-2.2000000000000002]
[null,"South",180,160,-2.2000000000000002,-5]
[null,"Southwest",225,252,0.6,-2.2000000000000002]
[null,"West",270,285,1.7,-1.1000000000000001]
[null,"Northwest",315,194,-0.6,-3.3]
[]
[null,"Flat","Flat",534,-3.3,-6.1]
[]
[]
[null,null,"Solar=C46:D52"]

{"sheet":"Weather_Stations","index":5,"n_rows":683,"n_cols":28,"rows_kept":683,"cut":false,"hidden":false,"merged":[[0,0,0,12],[0,18,1,22],[1,0,1,4]]}
["F280 weather data for Spreadsheet project (Interpreted from CSA_F280_Table 5_Final_2012-01-03.xls by Philip Jarrett Environment Canada)"]
["\"Jan 16, 2012 (All values rounded to zero decimal places)",null,null,null,null,"(Corrected Jan 16, 2012: Grimsby)",null,null,null,null,null,null,null,"Monthly Air Temperatures (Deg C)"]
["Seq","City","Region","DegDay","DHDBT","DCDBT","Strange","OHR","DGTEMP","JanWind","JulWind","Jan","Feb","Mar","Apr","May","Jun","Jul","Aug","Sep","Oct","Nov","Dec","Latidude","Longitude"]
[1,"Athabasca","AB",6000,-35,27,12,11,5,10,10,-15,-11,-4,4,11,14,16,15,10,4,-6,-13,54.72,-113.28,"AB","AB","Alberta"]
[2,"Banff","AB",5500,-31,27,14,7,5,10,8,-9,-7,-3,3,7,11,15,14,9,3,-4,-9,51.17,-115.57,"BC","BC","British Columbia"]
[3,"Barrhead","AB",5740,-33,27,12,11,5,8,9,-11,-11,-6,1,11,13,17,13,12,5,-3,-10,54.13,-114.4,"MB","MB","Manitoba"]
[4,"Beaverlodge","AB",5700,-36,28,12,9,5,10,12,-13,-10,-4,4,10,13,15,14,10,4,-6,-11,55.22,-119.43,"NB","NB","New Brunswick"]
[5,"Brooks","AB",4880,-32,32,14,10,7,13,12,-11,-7,-2,6,11,16,19,18,13,6,-2,-7,50.58,-111.88,"NL","NL","Newfoundland"]
[6,"Calgary","AB",5000,-30,28,12,8,6,15,14,-7,-5,-2,5,10,14,16,16,11,5,-3,-6,51.05,-114.08,"NS","NS","Nova Scotia"]
[7,"Campsie","AB",5750,-33,27,14,11,5,10,12,-14,-11,-4,4,10,14,16,15,10,4,-6,-12,54.13,-114.65,"NT","NT","N.W.T"]
[8,"Camrose","AB",5500,-33,29,13,10,5,11,12,-14,-10,-6,4,10,14,17,15,10,3,-5,-10,53.02,-112.83,"NU","NU","Nunavut"]
[9,"Canmore","AB",5400,-31,28,14,8,6,10,8,-10,-7,-3,3,7,11,15,14,9,3,-4,-9,51.09,-115.35,"ON","ON","Ontario"]
[10,"Cardston","AB",4700,-29,30,13,9,7,13,11,-5,-3,-1,5,10,14,18,17,12,6,0,-3,49.2,-113.3,"PE","PE","Prince Edward Island"]
[11,"Claresholm","AB",4680,-30,30,15,8,6,13,12,-8,-4,-2,5,10,14,18,17,12,6,-1,-5,50.03,-113.58,"QC","QC","Quebec"]
[12,"Cold Lake","AB",5860,-35,28,11,10,4,9,11,-16,-12,-5,4,10,15,17,16,10,3,-7,-13,54.45,-110.17,"SK","SK","Saskatchewan"]
[13,"Coleman","AB",5210,-31,29,15,8,7,14,10,-8,-5,-1,3,8,12,14,14,10,5,-3,-7,49.63,-114.5,"YT","YT","Yukon Territory"]
[14,"Coronation","AB",5640,-32,30,13,9,5,17,15,-14,-12,-5,4,10,14,17,16,10,4,-7,-12,52.08,-111.45]
[15,"Cowley","AB",4810,-29,29,15,8,6,26,18,-10,-6,-2,3,9,13,16,16,10,5,-2,-6,49.57,-114.08]
[16,"Drumheller","AB",5050,-32,30,14,8,5,7,10,-13,-8,-3,6,11,16,19,18,13,5,-3,-9,51.47,-112.7]
[17,"Edmonton","AB",5120,-30,28,10,10,5,11,12,-11,-8,-3,5,11,15,18,17,11,5,-4,-9,53.55,-113.47]
[18,"Edson","AB",5750,-34,27,13,9,5,7,8,-11,-8,-4,3,8,13,15,14,9,3,-6,-10,53.58,-116.43]
[19,"Embarras Portage","AB",7100,-41,28,11,10,3,10,12,-22,-17,-9,1,9,14,17,15,9,1,-10,-19,58.45,-111.47]
[20,"Fairview","AB",5840,-37,27,11,9,4,10,10,-14,-11,-5,4,11,14,16,15,10,4,-7,-12,56.07,-118.38]
[21,"Fort MacLeod","AB",4600,-30,31,15,9,8,21,16,-7,-4,0,6,11,15,18,17,12,7,-1,-6,49.72,-113.42]
[22,"Fort McMurray","AB",6250,-38,28,12,10,4,8,9,-18,-13,-6,3,10,15,17,15,10,2,-9,-15,56.73,-111.38]
[23,"Fort Saskatchewan","AB",5420,-32,28,13,10,5,13,12,-13,-10,-4,5,11,15,17,16,11,5,-6,-12,53.72,-113.22]
[24,"Fort Vermilion","AB",6700,-41,28,12,9,4,8,6,-22,-17,-10,2,11,15,17,15,9,2,-10,-20,58.4,-116]
[25,"Grande Prairie","AB",5790,-36,27,12,9,5,9,12,-14,-11,-5,4,10,14,16,15,10,4,-7,-11,55.17,-118.8]
[26,"Habay","AB",6750,-41,28,13,9,4,8,6,-26,-20,-14,2,11,14,15,14,7,2,-13,-18,58.83,-118.73]
[27,"Hardisty","AB",5640,-33,30,13,9,5,12,13,-17,-12,-7,3,11,15,16,17,9,5,-6,-13,52.67,-111.3]
[28,"High River","AB",4900,-31,28,15,8,6,17,15,-8,-6,-2,4,9,13,15,15,10,5,-2,-7,50.58,-113.87]
[29,"Hinton","AB",5500,-34,27,15,8,6,9,8,-12,-8,-4,3,8,11,14,13,9,4,-6,-8,53.4,-117.58]
[30,"Jasper","AB",5300,-31,28,12,8,6,9,8,-8,-5,-1,4,9,13,15,14,10,4,-4,-9,52.88,-118.08]
[31,"Keg River","AB",6520,-40,28,15,9,4,9,10,-19,-14,-7,3,9,14,15,14,9,1,-12,-16,57.75,-117.62]
[32,"Lac la Biche","AB",6100,-35,28,12,10,4,7,9,-16,-11,-6,3,10,14,17,16,11,4,-6,-13,54.77,-111.97]
[33,"Lacombe","AB",5500,-33,28,13,10,5,10,11,-13,-9,-5,4,9,13,16,15,10,4,-5,-9,52.47,-113.73]
[34,"Lethbridge","AB",4500,-30,31,14,9,8,20,15,-6,-4,0,6,11,15,18,18,13,7,-1,-5,49.7,-112.82]
[35,"Manning","AB",6300,-39,27,11,9,4,10,11,-18,-13,-7,3,10,14,16,15,10,2,-9,-14,56.92,-117.62]
[36,"Medicine Hat","AB",4540,-31,32,13,8,8,14,13,-9,-5,0,7,12,17,20,19,13,7,-2,-7,50.05,-110.67]
[37,"Peace River","AB",6050,-37,27,12,9,4,12,12,-15,-12,-6,4,10,14,16,15,10,3,-8,-12,56.23,-117.28]
[38,"Pincher Creek","AB",4740,-29,29,13,8,6,26,18,-6,-3,-2,4,9,13,17,17,12,6,-1,-4,49.48,-113.95]
[39,"Ranfurly","AB",5700,-34,29,12,10,5,12,12,-14,-12,-6,4,11,15,17,16,10,5,-6,-13,53.42,-111.68]
[40,"Red Deer","AB",5550,-32,28,13,10,5,12,12,-12,-9,-4,4,10,14,16,15,10,4,-5,-10,52.27,-113.8]
[41,"Rocky Mountain House","AB",5640,-32,27,13,9,5,7,8,-12,-9,-5,3,8,12,15,14,9,3,-6,-10,52.37,-114.92]
[42,"Slave Lake","AB",5850,-35,26,11,11,4,15,12,-13,-10,-5,3,9,14,16,15,10,3,-6,-12,55.28,-114.77]
[43,"Stettler","AB",5300,-32,30,14,9,5,16,13,-13,-9,-3,5,10,14,16,16,11,5,-5,-11,52.32,-112.72]
[44,"Stony Plain","AB",5300,-32,28,11,10,5,11,10,-12,-8,-3,5,11,15,16,16,11,5,-4,-10,53.53,-114]
[45,"Suffield","AB",4770,-31,32,15,10,8,18,18,-11,-7,-1,6,12,16,19,19,13,7,-3,-9,50.2,-111.17]
[46,"Taber","AB",4580,-31,31,15,9,8,19,13,-9,-4,-1,6,12,16,19,18,13,7,-1,-6,49.78,-112.15]
[47,"Turner Valley","AB",5220,-31,28,15,8,5,17,15,-10,-7,-3,2,7,11,13,13,9,4,-3,-9,50.67,-114.28]
[48,"Valleyview","AB",5600,-37,27,13,9,4,15,13,-13,-9,-2,5,10,14,16,15,10,5,-4,-11,55.07,-117.28]
[49,"Vegreville","AB",5780,-34,29,13,10,5,12,13,-15,-11,-6,4,10,14,17,15,10,3,-6,-11,53.5,-112.05]
[50,"Vermilion","AB",5740,-35,29,13,10,5,12,12,-18,-14,-7,4,11,15,16,15,10,4,-5,-14,53.37,-110.85]
[51,"Wagner","AB",5850,-35,26,12,11,4,15,12,-13,-10,-5,3,9,14,16,15,10,3,-6,-12,55.35,-114.98]
[52,"Wainwright","AB",5700,-33,29,12,10,5,12,13,-14,-9,-6,5,10,15,18,17,11,4,-4,-11,52.82,-110.87]
[53,"Wetaskiwin","AB",5500,-33,29,13,10,5,10,11,-15,-11,-6,3,11,15,16,16,9,5,-6,-12,52.97,-113.37]
[54,"Whitecourt","AB",5650,-33,27,12,11,5,7,8,-12,-8,-3,4,10,14,16,14,9,4,-7,-11,54.15,-115.68]
[55,"Wimborne","AB",5310,-31,29,13,8,5,15,14,-13,-9,-6,2,10,14,16,15,10,4,-5,-9,51.87,-113.58]
[56,"100 Mile House","BC",5030,-30,29,15,7,8,10,8,-8,-4,0,5,9,13,15,15,10,5,-2,-8,51.65,-121.2833]
[57,"Abbotsford","BC",2860,-8,29,11,11,11,10,8,4,5,7,10,13,16,18,18,15,11,6,3,49.051699999999997,-122.3289]
[58,"Agassiz","BC",2750,-9,31,10,12,11,13,12,3,5,7,11,14,16,19,19,16,11,6,4,49.23,-121.77]
[59,"Alberni","BC",3100,-5,31,13,9,10,4,9,2,3,6,9,12,15,18,18,15,10,5,2,49.27,-124.8]
[60,"Ashcroft","BC",3700,-24,34,14,9,10,5,10,-7,-2,4,10,14,18,21,20,16,9,0,-3,50.72,-121.28]
[61,"Bamfield","BC",3080,-2,23,8,10,11,14,10,5,6,6,8,11,13,14,15,14,10,7,5,48.83,-125.13]
[62,"Beatton River","BC",6300,-37,26,13,10,4,4,6,-15,-10,-8,1,7,12,14,12,7,1,-8,-12,57.38,-121.4]
[63,"Bella Bella","BC",3180,-5,23,8,11,10,15,9,3,4,4,6,10,12,14,15,13,9,5,1,52.16,-128.13999999999999]
[64,"Bella Coola","BC",3560,-14,27,11,11,10,8,11,-1,1,5,8,12,14,17,17,13,8,3,-1,52.37,-126.75]
[65,"Burnaby (Simon Fraser Univ.)","BC",3100,-7,25,7,9,11,12,11,3,4,6,9,12,14,17,17,15,10,5,3,49.28,-122.92]
[66,"Burns Lake","BC",5450,-31,26,16,8,6,5,6,-11,-7,-3,3,8,12,13,12,8,3,-4,-9,54.23,-125.75]
[67,"Cache Creek","BC",3700,-24,34,16,9,10,5,10,-5,-1,4,9,13,17,20,19,15,8,0,-4,50.8,-121.32]
[68,"Campbell River","BC",3000,-5,26,9,10,10,9,9,4,5,6,9,12,15,17,17,14,10,6,4,50.02,-125.24]
[69,"Carmi","BC",4750,-24,31,19,9,10,5,6,-7,-3,1,6,10,13,16,15,11,5,-2,-7,49.5,-119.12]
[70,"Castlegar","BC",3580,-18,32,15,10,10,9,8,-3,0,4,9,13,17,20,20,14,8,2,-2,49.32,-117.67]
[71,"Chetwynd","BC",5500,-35,27,14,9,5,9,8,-11,-8,-2,5,10,13,15,15,10,4,-6,-9,55.7,-121.63]
[72,"Chilliwack","BC",2780,-9,30,11,11,11,13,12,2,5,7,10,13,16,18,18,16,11,6,3,49.166699999999999,-121.95]
[73,"Cloverdale","BC",2700,-8,29,10,11,11,9,7,4,5,8,11,14,16,18,19,16,11,6,3,49.1,-122.7333]
[74,"Comox","BC",3100,-7,27,8,9,10,13,12,4,4,6,9,12,15,18,18,14,10,6,4,49.68,-124.93]
[75,"Courtenay","BC",3100,-7,28,8,9,10,13,12,4,4,6,9,12,15,18,18,14,10,6,4,49.68,-124.98]
[76,"Cranbrook","BC",4400,-26,32,13,7,9,6,11,-6,-3,2,7,11,15,19,18,13,6,-1,-7,49.5,-115.77]
[77,"Crescent Valley","BC",3650,-18,31,17,10,10,9,8,-4,-1,4,8,13,16,19,19,14,8,1,-3,49.45,-117.55]
[78,"Crofton","BC",2880,-4,28,13,10,11,8,10,2,4,5,8,12,14,18,18,15,10,6,4,48.87,-123.65]
[79,"Dawson Creek","BC",5900,-38,27,13,9,5,10,10,-15,-11,-5,4,9,13,15,14,10,4,-7,-12,55.77,-120.23]
[80,"Dease Lake","BC",6730,-37,24,11,7,4,7,7,-14,-12,-5,1,7,11,13,11,7,0,-10,-14,58.44,-130]
[81,"Dog Creek","BC",4800,-28,29,16,7,6,10,8,-9,-4,0,7,10,14,17,16,14,6,-3,-5,51.58,-122.3]
[82,"Duncan","BC",2980,-6,28,14,10,10,4,9,3,4,6,8,12,15,17,17,14,9,5,3,48.78,-123.7]
[83,"Elko","BC",4600,-28,30,14,9,9,10,8,-7,-3,1,6,11,15,18,18,13,6,-1,-6,49.3,-115.12]
[84,"Fernie","BC",4750,-27,30,15,9,8,10,8,-7,-4,0,5,10,13,16,16,11,5,-1,-6,49.5,-115.07]
[85,"Fort Nelson","BC",6710,-39,28,12,9,4,4,7,-21,-15,-8,3,10,15,17,15,9,0,-13,-18,58.83,-122.7]
[86,"Fort St. John","BC",5750,-35,26,10,10,5,14,12,-13,-9,-5,4,10,14,16,15,10,3,-7,-10,56.25,-120.85]
[87,"Glacier","BC",5800,-27,27,12,8,8,10,8,-10,-7,-2,2,6,10,13,13,8,2,-5,-9,51.27,-117.52]
[88,"Gold River","BC",3230,-8,31,13,8,11,4,9,1,3,5,8,12,15,18,18,15,9,4,2,49.78,-126.05]
[89,"Golden","BC",4750,-27,30,14,7,8,3,5,-10,-5,0,6,11,15,17,17,11,5,-2,-8,51.3,-116.97]
[90,"Grand Forks","BC",3820,-19,34,16,9,10,9,8,-5,-1,4,9,13,16,20,19,14,7,1,-4,49.03,-118.45]
[91,"Greenwood","BC",4100,-20,34,17,9,10,9,8,-8,-3,1,6,10,14,18,17,11,6,0,-5,49.1,-118.68]
[92,"Haney","BC",2840,-9,30,12,11,11,9,7,2,4,7,9,12,15,18,18,15,10,5,3,49.22,-122.6]
[93,"Hope","BC",3000,-13,31,10,10,11,15,13,2,4,7,10,13,16,19,19,16,10,5,2,49.38,-121.44]
[94,"Jordan River","BC",2900,-1,22,7,10,12,14,10,6,7,8,10,12,13,15,15,14,11,8,6,48.42,-124.05]
[95,"Kamloops","BC",3450,-23,34,13,9,10,10,10,-3,0,5,10,15,18,21,21,15,8,2,-2,50.67,-120.32]
[96,"Kaslo","BC",3830,-17,30,13,9,9,10,8,-3,-1,3,7,12,15,18,18,13,7,2,-2,49.92,-116.92]
[97,"Kelowna","BC",3400,-17,33,15,9,11,5,6,-3,-1,4,8,13,17,19,19,14,7,1,-3,49.88,-119.48]
[98,"Kimberley","BC",4650,-25,31,16,8,8,6,11,-7,-4,1,6,11,14,18,17,13,6,-2,-7,49.68,-115.98]
[99,"Kitimat Plant","BC",3750,-16,25,10,8,7,5,7,-2,0,4,7,11,14,17,17,13,8,2,-1,54.05,-128.63]
[100,"Kitimat Townsite","BC",3900,-16,24,10,8,9,5,7,-3,-1,3,6,10,14,16,16,12,7,2,-1,54.07,-128.65]
[101,"Ladner","BC",2600,-6,27,7,11,12,11,11,4,5,7,10,13,16,18,18,15,10,6,4,49.08,-123.08]
[102,"Ladysmith","BC",3000,-7,27,12,11,11,8,10,3,4,6,9,12,15,18,18,15,10,5,3,48.99,-123.82]
[103,"Langford","BC",2750,-4,27,10,11,12,10,8,6,6,8,10,12,15,16,16,15,11,8,6,48.45,-123.5]
[104,"Langley","BC",2700,-8,29,11,11,11,9,7,4,5,8,11,14,16,18,19,16,11,6,3,49.1,-122.65]
[105,"Lillooet","BC",3400,-21,34,13,9,11,14,23,-2,1,5,10,15,19,23,22,17,10,3,-1,50.68,-121.93]
[106,"Lytton","BC",3300,-17,35,12,9,11,14,23,-1,2,6,10,15,18,22,22,17,10,3,-2,50.23,-121.57]
[107,"Mackenzie","BC",5550,-34,27,12,8,5,7,7,-11,-7,-4,3,9,14,15,14,10,3,-4,-8,55.3,-123.08]
[108,"Masset","BC",3700,-5,17,7,10,10,14,15,1,3,4,6,8,10,13,13,12,9,5,3,54.02,-132.1]
[109,"McBride","BC",4980,-29,29,14,8,8,8,6,-7,-4,0,5,9,13,15,15,10,5,-2,-6,53.3,-120.17]
[110,"McLeod Lake","BC",5450,-35,27,12,8,5,7,7,-11,-7,-4,3,9,14,15,14,10,3,-4,-8,54.98,-123.03]
[111,"Merritt","BC",3900,-24,34,15,9,11,10,10,-4,-1,4,8,12,15,18,18,14,8,1,-4,50.1,-120.7833]
[112,"Mission City","BC",2850,-9,30,10,11,11,10,8,2,5,7,10,13,15,18,18,16,11,6,3,49.13,-122.3]
[113,"Montrose","BC",3600,-16,32,17,10,10,8,8,-4,-1,3,8,13,17,20,20,14,7,2,-3,49.08,-117.58]
[114,"Nakusp","BC",3560,-20,31,12,10,9,5,5,-2,0,3,8,12,16,20,19,14,8,2,-1,50.23,-117.8]
[115,"Nanaimo","BC",3000,-6,27,9,11,11,8,10,2,4,5,8,12,14,18,18,15,10,6,4,49.17,-123.93]
[116,"Nelson","BC",3500,-18,31,13,10,10,10,8,-1,1,4,8,12,16,20,20,15,8,3,-1,49.48,-117.28]
[117,"New Westminster","BC",2800,-8,29,10,10,11,9,7,2,5,6,9,12,15,18,18,15,11,6,4,49.22,-122.92]
[118,"North Vancouver","BC",2910,-7,26,10,11,11,7,8,4,5,7,10,13,15,18,18,15,10,6,3,49.32,-123.07]
[119,"Ocean Falls","BC",3400,-10,23,7,10,8,18,13,1,2,4,6,10,13,15,16,14,9,4,2,52.35,-127.7]
[120,"Osoyoos","BC",3100,-14,35,15,10,12,7,6,-1,2,6,11,15,19,23,22,17,10,3,-1,49.03,-119.5]
[121,"Parksville","BC",3200,-6,26,9,11,12,8,10,4,5,6,9,12,15,18,18,14,10,6,3,49.32,-124.33]
[122,"Penticton","BC",3350,-15,33,13,9,11,14,9,-1,1,5,9,14,18,21,20,15,9,3,-1,49.5,-119.58]
[123,"Port Alberni","BC",3100,-5,31,13,9,10,4,9,2,3,6,9,12,15,18,18,15,10,5,2,49.2333,-124.8]
[124,"Port Alice","BC",3010,-3,26,9,8,11,4,9,4,5,6,8,11,13,16,16,14,10,6,4,50.38,-127.45]
[125,"Port Hardy","BC",3440,-5,20,7,10,10,15,9,4,4,6,7,10,12,14,14,12,9,6,4,50.7,-127.42]
[126,"Port McNeill","BC",3410,-5,22,8,10,10,15,9,4,4,5,8,10,12,14,14,13,10,6,4,50.58,-127.1]
[127,"Port Renfrew","BC",2900,-3,24,9,9,11,14,10,3,5,6,8,11,13,15,15,13,10,6,4,48.56,-124.4]
[128,"Powell River","BC",3100,-7,26,8,10,11,7,7,4,5,7,9,13,16,18,18,16,11,7,4,49.83,-124.52]
[129,"Prince George","BC",4720,-32,28,12,9,6,10,8,-8,-5,0,5,10,14,16,15,10,4,-3,-7,53.92,-122.75]
[130,"Prince Rupert","BC",3900,-13,19,6,9,10,14,10,2,3,4,6,9,12,13,14,12,8,4,3,54.32,-130.32]
[131,"Princeton","BC",4250,-24,33,16,8,10,2,7,-5,-3,2,7,11,15,19,18,14,6,-1,-5,49.5,-120.51]
[132,"Qualicum Beach","BC",3200,-7,27,10,11,10,8,10,3,4,6,8,12,15,17,17,13,9,5,3,49.35,-124.45]
[133,"Queen Charlotte City","BC",3520,-6,21,5,9,10,17,11,4,4,5,7,9,12,14,15,13,9,6,4,53.26,-132.08000000000001]
[134,"Quesnel","BC",4650,-31,30,14,7,6,6,5,-7,-4,1,6,11,15,17,16,11,6,-2,-6,52.98,-122.48]
[135,"Revelstoke","BC",4000,-20,31,12,9,9,5,5,-4,-2,2,8,13,16,19,18,13,7,1,-3,50.98,-118.2]
[136,"Richmond","BC",2800,-7,27,7,11,11,11,11,4,5,7,10,13,16,18,18,15,10,6,4,49.17,-123.1]
[137,"Salmon Arm","BC",3650,-19,33,14,11,10,4,5,-2,0,4,9,13,17,21,20,14,8,2,-2,50.7,-119.28]
[138,"Sandspit","BC",3450,-4,18,5,9,11,22,16,4,4,5,7,9,12,14,15,13,9,6,4,53.25,-131.82]
[139,"Sechelt","BC",2680,-6,27,9,12,12,8,10,4,5,6,9,12,14,17,17,14,10,6,5,49.47,-123.75]
[140,"Sidney","BC",2850,-4,26,10,10,12,10,8,5,5,7,9,12,15,17,17,14,10,6,4,48.65,-123.4]
[141,"Smith River","BC",7100,-45,26,11,8,4,5,10,-25,-16,-10,0,7,13,14,13,7,-1,-13,-21,59.88,-126.43]
[142,"Smithers","BC",5040,-29,26,12,8,6,7,6,-8,-4,0,5,9,13,15,14,10,4,-2,-7,54.783299999999997,-127.16670000000001]
[143,"Sooke","BC",2900,-1,21,6,9,11,11,12,5,5,7,8,10,12,14,14,13,9,6,4,48.38,-123.72]
[144,"Squamish","BC",2950,-9,29,11,11,11,5,6,2,4,6,9,12,15,18,18,15,9,4,2,49.7,-123.15]
[145,"Stewart","BC",4350,-17,25,9,8,8,3,4,-4,-1,2,6,10,14,15,14,11,6,1,-3,55.93,-129.97999999999999]
[146,"Surrey (88 Ave & 156 St.)","BC",2750,-8,29,11,11,12,9,7,4,5,8,11,14,16,18,19,16,11,6,3,49.162799999999997,-122.7902]
[147,"Tahsis","BC",3150,-4,26,12,10,11,4,9,2,4,6,8,12,15,18,19,15,10,5,2,49.93,-126.65]
[148,"Taylor","BC",5720,-35,26,13,10,5,14,12,-13,-9,-5,4,10,14,16,15,10,3,-7,-10,56.2,-120.69]
[149,"Terrace","BC",4150,-19,27,9,8,7,18,12,-3,-1,2,6,10,14,16,16,12,6,1,-2,54.52,-128.6]
[150,"Tofino","BC",3150,-2,20,8,10,11,10,9,5,5,6,8,10,12,14,15,13,10,7,5,49.12,-125.88]
[151,"Trail","BC",3600,-14,33,14,9,10,8,8,-3,0,4,9,13,17,20,20,15,8,2,-2,49.1,-117.7]
[152,"Ucluelet","BC",3120,-2,18,5,11,11,18,13,6,6,7,9,11,13,14,15,14,11,8,6,48.93,-125.55]
[153,"Vancouver (city hall)","BC",2825,-7,28,7,11,11,11,11,3,5,6,9,12,15,18,18,15,10,6,4,49.25,-123.12]
[154,"Vancouver (Granville & 41 Ave)","BC",2925,-6,28,9,11,12,11,11,3,5,6,9,12,15,18,18,15,10,6,4,49.234299999999998,-123.1396]
[155,"Vernon","BC",3600,-20,33,13,9,10,10,12,-3,0,4,9,13,17,21,20,15,8,2,-2,50.3,-119.27]
[156,"Victoria","BC",2650,-4,24,10,9,12,15,15,6,6,8,10,12,15,16,16,15,11,8,6,48.43,-123.37]
[157,"Victoria Gonzales Height","BC",2700,-4,24,7,9,12,15,15,6,6,8,10,12,15,16,16,15,11,8,6,48.42,-123.32]
[158,"Victoria Mt Tolmie","BC",2700,-6,24,9,8,13,7,6,6,6,8,10,13,16,19,18,16,11,7,5,48.47,-123.33]
[159,"West Vancouver","BC",2950,-7,28,9,10,12,5,4,4,5,7,9,12,15,18,18,15,10,6,4,49.33,-123.17]
[160,"Whistler","BC",4180,-17,30,14,11,9,3,5,-3,-1,2,6,10,13,16,16,12,7,1,-3,50.12,-122.96]
[161,"White Rock","BC",2620,-5,25,8,13,12,7,5,5,6,8,10,13,16,18,18,15,11,7,5,49.02,-122.8]
[162,"Williams Lake","BC",4400,-30,29,12,7,7,10,8,-7,-4,0,5,10,13,16,15,11,5,-3,-7,52.133299999999998,-122.15]
[163,"Youbou","BC",3050,-5,31,12,9,10,4,9,3,4,6,8,12,15,17,18,15,10,5,3,48.88,-124.2]
[164,"Beausejour","MB",5680,-33,29,13,15,6,13,11,-18,-14,-6,4,12,17,19,18,12,5,-5,-15,50.066699999999997,-96.5167]
[165,"Boissevain","MB",5500,-32,30,12,15,6,14,12,-17,-13,-5,4,12,17,19,18,13,6,-4,-13,49.2333,-100.05]
[166,"Brandon","MB",5760,-33,30,13,13,6,15,12,-17,-13,-6,4,11,16,18,18,12,4,-6,-14,49.833300000000001,-99.95]
[167,"Churchill","MB",8950,-38,25,8,10,-1,22,18,-27,-25,-19,-10,-1,7,12,12,6,-1,-13,-22,58.75,-94.12]
[168,"Dauphin","MB",5900,-33,30,12,13,5,15,13,-16,-12,-6,4,11,16,19,18,12,5,-6,-13,51.15,-100.05]
[169,"Flin Flon","MB",6440,-38,27,10,12,4,9,11,-20,-15,-8,2,10,16,19,17,10,3,-8,-18,54.77,-101.88]
[170,"Gimli","MB",5800,-34,29,11,15,6,15,13,-17,-14,-7,3,10,16,19,18,12,5,-5,-14,50.64,-96.99]
[171,"Island Lake","MB",6900,-36,27,9,12,4,10,10,-22,-19,-11,-1,8,14,18,17,10,2,-8,-17,53.866700000000002,-94.666700000000006]
[172,"Lac du Bonnet","MB",5730,-34,29,12,15,6,8,8,-17,-13,-6,3,10,16,19,18,13,5,-4,-11,50.27,-96.06]
[173,"Lynn Lake","MB",7770,-40,27,11,11,2,11,11,-24,-20,-13,-3,6,13,16,15,8,-1,-13,-21,56.85,-101.05]
[174,"Morden","MB",5400,-31,30,12,16,7,13,11,-16,-12,-5,5,13,18,20,19,13,6,-4,-12,49.183300000000003,-98.1]
[175,"Neepawa","MB",5760,-32,29,12,15,6,15,12,-17,-13,-6,3,12,17,19,18,12,5,-5,-14,50.2333,-99.466700000000003]
[176,"Pine Falls","MB",5900,-34,28,12,16,6,9,9,-19,-15,-7,4,12,16,19,18,12,5,-5,-16,50.566699999999997,-96.216700000000003]
[177,"Portage la Prairie","MB",5600,-31,30,12,15,6,14,11,-15,-12,-5,5,12,17,20,19,12,5,-6,-13,50,-98.29]
[178,"Rivers","MB",5840,-34,29,14,15,6,16,15,-14,-14,-5,5,13,17,19,17,12,4,-6,-14,50.033299999999997,-100.2333]
[179,"Sandilands","MB",5650,-32,29,13,15,6,15,13,-17,-12,-5,4,12,17,19,18,12,5,-6,-13,49.36,-96.3]
[180,"Selkirk","MB",5700,-33,29,12,15,6,13,11,-17,-13,-6,4,12,17,20,19,13,6,-5,-14,50.15,-96.866699999999994]
[181,"Split Lake","MB",7900,-38,27,11,11,1,13,13,-24,-21,-13,-3,6,13,16,15,8,0,-13,-22,56.25,-96.1]
[182,"Steinbach","MB",5700,-33,29,13,15,6,16,14,-17,-13,-6,4,12,17,19,18,12,5,-5,-14,49.533299999999997,-96.683300000000003]
[183,"Swan River","MB",6100,-34,29,13,14,5,12,10,-17,-14,-8,3,10,15,18,17,12,4,-6,-13,52.14,-101.27]
[184,"The Pas","MB",6480,-36,28,10,13,5,13,13,-19,-16,-9,1,9,15,18,17,11,3,-8,-16,53.87,-101.25]
[185,"Thompson","MB",7600,-40,27,13,11,2,11,11,-24,-20,-12,-2,6,13,16,15,8,0,-12,-21,55.79,-97.86]
[186,"Virden","MB",5620,-33,30,13,15,6,16,15,-17,-12,-5,4,12,17,19,18,12,5,-5,-14,49.86,-100.93]
[187,"Winnipeg","MB",5670,-33,30,12,15,6,18,15,-16,-13,-6,4,12,17,20,19,13,5,-5,-13,49.89,-97.15]
[188,"Alma","NB",4500,-21,26,10,12,7,18,16,-7,-7,-2,4,9,14,17,17,13,8,3,-4,45.6,-64.95]
[189,"Bathurst","NB",5020,-23,30,11,13,7,17,12,-11,-10,-4,2,10,16,19,18,13,7,1,-8,47.6,-65.650000000000006]
[190,"Campbellton","NB",5500,-26,29,11,14,7,16,12,-13,-10,-4,2,9,16,19,17,12,6,0,-9,48,-66.67]
[191,"Edmundston","NB",5320,-27,28,12,14,7,13,9,-13,-12,-4,2,10,16,19,17,12,6,-1,-10,47.37,-68.33]
[192,"Fredericton","NB",4670,-24,29,12,14,8,13,10,-10,-8,-2,4,11,16,19,19,14,8,2,-6,45.95,-66.650000000000006]
[193,"Gagetown","NB",4460,-24,29,11,14,8,14,11,-9,-7,-2,5,11,16,20,19,14,8,2,-5,45.79,-66.16]
[194,"Grand Falls","NB",5300,-27,28,11,14,7,13,9,-13,-11,-5,3,11,15,18,17,12,6,-1,-10,47.05,-67.73]
[195,"Miramichi","NB",4950,-24,30,11,13,7,14,12,-10,-9,-3,3,10,15,19,18,13,7,0,-8,47.03,-65.47]
[196,"Moncton","NB",4680,-23,28,11,13,8,19,13,-9,-8,-3,3,10,15,19,18,14,8,2,-5,46.1,-64.78]
[197,"Oromocto","NB",4650,-24,29,11,14,8,13,11,-9,-8,-2,5,11,16,19,19,14,8,2,-5,45.84,-66.48]
[198,"Sackville","NB",4590,-22,27,10,13,8,19,17,-8,-7,-2,4,9,14,18,18,14,8,2,-4,45.88,-64.37]
[199,"Saint Andrews","NB",4680,-22,25,10,13,8,15,8,-8,-7,-2,4,10,14,17,17,13,8,3,-4,45.07,-67.05]
[200,"Saint George","NB",4680,-21,25,11,13,8,13,7,-8,-7,-2,5,11,16,18,18,14,8,2,-5,45.13,-66.819999999999993]
[201,"Saint John","NB",4570,-22,25,10,13,7,18,13,-8,-7,-2,4,10,14,17,17,13,8,3,-4,45.2667,-66.05]
[202,"Shippagan","NB",4930,-22,28,9,13,2,22,13,-10,-10,-4,2,9,15,19,18,14,7,1,-5,47.73,-64.7]
[203,"St. Stephen","NB",4700,-24,28,13,14,7,8,6,-8,-7,-2,5,11,16,18,18,14,8,2,-5,45.2,-67.28]
[204,"Woodstock","NB",4910,-26,30,13,13,8,13,10,-12,-10,-3,4,11,16,19,18,13,7,0,-8,46.16,-67.599999999999994]
[205,"Argentia","NL",4600,-12,21,5,12,8,29,18,-3,-3,-1,3,6,10,14,16,13,9,5,1,47.3,-53.98]
[206,"Bonavista","NL",5000,-14,24,7,12,7,39,25,-5,-5,-3,1,6,10,15,16,12,8,3,-1,48.65,-53.12]
[207,"Buchans","NL",5250,-24,27,9,12,6,24,17,-8,-9,-5,1,7,12,16,16,11,5,0,-5,48.816699999999997,-56.866700000000002]
[208,"Cape Harrison","NL",6900,-29,26,8,7,5,24,17,-16,-15,-10,-3,3,7,12,12,9,3,-3,-10,54.78,-57.95]
[209,"Cape Race","NL",4900,-11,19,5,13,7,34,22,-3,-4,-2,1,4,8,12,15,12,8,4,0,46.65,-53.07]
[210,"Channel-Port aux Basques","NL",5000,-13,19,6,13,7,32,19,-5,-6,-3,1,5,9,14,15,12,7,3,-2,47.57,-59.15]
[211,"Corner Brook","NL",4760,-16,26,9,12,8,12,9,-7,-7,-4,2,8,13,17,17,13,7,2,-3,48.95,-57.95]
[212,"Gander","NL",5110,-18,27,9,12,7,24,17,-7,-7,-4,2,7,12,16,16,12,6,1,-4,48.98,-54.59]
[213,"Grand Bank","NL",4550,-14,20,7,12,8,29,18,-4,-5,-2,2,6,11,15,16,13,8,4,0,47.1,-55.77]
[214,"Grand Falls","NL",5020,-26,27,11,12,7,24,17,-8,-8,-4,2,8,13,17,17,12,6,1,-4,48.93,-55.67]
[215,"Happy Valley-Goose Bay","NL",6670,-31,27,10,11,5,17,13,-18,-16,-9,-1,6,11,15,15,10,3,-4,-13,53.32,-60.37]
[216,"Labrador City","NL",7710,-36,24,10,9,3,14,13,-23,-21,-14,-5,4,10,14,12,7,0,-9,-19,52.95,-66.92]
[217,"St. Anthony","NL",6440,-25,22,7,11,5,27,20,-11,-11,-7,-1,4,8,13,14,10,4,-1,-7,51.37,-55.58]
[218,"St. John's","NL",4800,-15,24,8,13,7,28,21,-5,-5,-3,2,6,11,16,16,12,7,3,-2,47.57,-52.72]
[219,"Stephenville","NL",4850,-16,24,7,12,8,25,14,-6,-7,-4,3,8,12,16,17,13,8,3,-2,48.55,-58.58]
[220,"Twin Falls","NL",7790,-35,24,9,9,4,14,12,-22,-21,-13,-4,4,10,14,13,8,1,-8,-17,53.5,-64.53]
[221,"Wabana","NL",4750,-15,24,8,13,7,27,20,-5,-5,-3,2,6,11,16,16,12,7,3,-2,47.63,-52.95]
[222,"Wabush","NL",7710,-36,24,10,9,3,14,13,-23,-21,-14,-5,4,10,14,12,7,0,-9,-19,52.92,-66.87]
[223,"Amherst","NS",4500,-21,27,9,13,8,19,17,-8,-6,-2,4,10,15,18,18,14,8,3,-3,45.83,-64.2]
[224,"Antigonish","NS",4510,-17,27,11,13,8,18,15,-7,-5,-2,4,9,14,19,18,14,8,4,-2,45.62,-62]
[225,"Bridgewater","NS",4140,-15,27,13,12,7,19,15,-5,-5,0,5,10,15,19,19,14,8,4,-2,44.38,-64.52]
[226,"Canso","NS",4400,-13,25,6,13,8,23,17,-3,-4,-1,3,7,12,17,18,16,10,5,1,45.33,-61]
[227,"Dartmouth","NS",4100,-16,26,8,12,8,18,11,-5,-4,-1,4,9,14,18,18,15,10,5,-1,44.67,-63.57]
[228,"Debert","NS",4500,-21,27,12,13,7,17,12,-7,-6,-2,4,10,15,19,18,14,8,3,-4,45.43,-63.47]
[229,"Digby","NS",4020,-15,25,9,13,9,18,14,-4,-4,0,5,11,15,18,18,14,9,5,-1,44.62,-65.77]
[230,"Greenwood (CFB)","NS",4140,-18,29,11,14,7,18,12,-5,-5,-1,5,11,16,20,19,15,9,4,-2,44.98,-64.900000000000006]
[231,"Halifax","NS",4000,-16,26,8,12,8,18,11,-5,-4,-1,4,9,14,18,18,15,10,5,-1,44.65,-63.6]
[232,"Kentville","NS",4130,-18,28,11,13,9,12,8,-4,-3,0,5,11,17,20,19,16,9,4,-1,45.08,-64.5]
[233,"Liverpool","NS",3990,-16,27,7,12,9,22,15,-4,-3,0,4,8,12,15,16,14,10,5,0,44.03,-64.72]
[234,"Lockeport","NS",4000,-14,25,6,13,9,22,15,2,2,1,0,-1,-1,-2,-1,0,1,1,2,43.7,-65.12]
[235,"Louisburg","NS",4530,-15,26,8,12,8,22,18,-5,-5,-2,2,7,12,16,17,14,9,4,-2,45.92,-59.98]
[236,"Lunenburg","NS",4140,-15,26,7,12,8,22,15,-4,-3,0,4,8,12,15,16,14,10,5,0,44.38,-64.319999999999993]
[237,"New Glasgow","NS",4320,-19,27,11,13,7,19,15,-7,-7,-2,3,10,16,19,18,14,8,3,-3,45.58,-62.65]
[238,"North Sydney","NS",4500,-16,27,10,13,8,21,16,-5,-6,-3,2,8,13,18,18,14,9,4,-2,46.22,-60.25]
[239,"Pictou","NS",4310,-19,27,10,13,8,19,15,-7,-7,-2,3,9,16,19,19,14,8,3,-2,45.68,-62.72]
[240,"Port Hawkesbury","NS",4500,-17,27,9,13,8,19,13,-6,-8,-3,3,8,14,18,18,14,9,4,-3,45.62,-61.35]
[241,"Springhill","NS",4540,-20,27,9,13,7,19,17,-7,-7,-3,3,10,15,19,18,14,8,2,-4,45.65,-64.05]
[242,"Stewiacke","NS",4400,-20,27,11,13,7,19,14,-5,-4,-1,5,11,15,19,19,14,8,3,-2,45.13,-63.35]
[243,"Sydney","NS",4530,-16,27,9,13,8,21,16,-5,-6,-3,2,8,13,18,18,14,9,4,-2,46.15,-60.18]
[244,"Tatamagouche","NS",4380,-20,27,11,13,8,19,15,-7,-6,-2,3,10,16,19,19,14,8,3,-3,45.72,-63.3]
[245,"Truro","NS",4500,-20,27,12,13,7,14,10,-7,-7,-2,4,10,15,18,18,13,8,3,-4,45.37,-63.27]
[246,"Wolfville","NS",4140,-19,28,11,13,9,12,8,-4,-3,0,5,11,17,20,19,16,9,4,-1,45.08,-64.37]
[247,"Yarmouth","NS",3990,-14,22,7,13,9,22,14,-3,-3,0,5,10,14,17,17,14,10,5,0,43.83,-66.12]
[248,"Aklavik","NT",9600,-42,26,9,8,-2,7,11,-27,-25,-21,-13,0,11,14,11,4,-8,-21,-26,68.23,-135.01]
[249,"Echo Bay / Port Radium","NT",9300,-42,22,8,9,-1,9,9,-29,-28,-21,-11,3,12,13,10,5,-2,-15,-23,66.05,-117.88]
[250,"Fort Good Hope","NT",8700,-43,28,11,9,0,4,8,-27,-23,-20,-6,5,15,17,13,7,-4,-19,-23,66.290000000000006,-128.63]
[251,"Fort McPherson","NT",9150,-44,26,9,8,-2,7,11,-28,-24,-20,-10,2,13,15,12,4,-8,-21,-25,67.430000000000007,-134.88]
[252,"Fort Providence","NT",7620,-40,28,13,9,3,5,7,-24,-19,-14,-2,6,14,17,14,9,-1,-12,-20,61.35,-117.65]
[253,"Fort Resolution","NT",7750,-40,26,11,10,2,12,11,-25,-21,-15,-3,6,13,16,14,7,0,-10,-21,61.19,-113.67]
[254,"Fort Simpson","NT",7660,-42,28,11,10,2,8,9,-25,-20,-13,0,8,15,17,15,8,-2,-16,-22,61.93,-121.35]
[255,"Fort Smith","NT",7300,-41,28,11,10,3,10,10,-23,-19,-12,0,8,14,17,14,8,0,-12,-19,60,-111.88]
[256,"Hay River","NT",7550,-38,27,9,9,3,12,12,-22,-20,-14,-3,5,12,16,14,9,0,-12,-18,60.85,-115.7333]
[257,"Inuvik","NT",9600,-43,26,9,8,-2,7,11,-27,-26,-22,-12,0,12,14,11,4,-8,-21,-24,68.349999999999994,-133.72]
[258,"Mould Bay","NT",12900,-44,11,4,5,-9,14,18,-34,-34,-31,-24,-11,0,4,1,-6,-18,-28,-31,76.23,-119.33]
[259,"Norman Wells","NT",8510,-43,28,10,9,0,10,12,-26,-24,-18,-6,6,15,17,14,7,-5,-19,-23,65.283299999999997,-126.85]
[260,"Rae-Edzo","NT",8300,-42,25,9,9,0,12,14,-27,-21,-18,-6,4,13,16,13,7,-3,-14,-22,62.83,-116.05]
[261,"Tungsten","NT",7700,-49,26,11,7,2,11,9,-20,-18,-13,-4,3,9,12,9,4,-3,-15,-19,61.95,-128.27000000000001]
[262,"Ulukhaqtuuq / Holman","NT",10700,-39,18,6,6,-5,19,18,-29,-28,-25,-17,-7,5,9,7,0,-9,-20,-26,70.73,-117.75]
[263,"Wrigley","NT",8050,-42,28,13,9,0,8,9,-27,-23,-16,-2,8,15,17,13,7,-4,-19,-25,63.23,-123.47]
[264,"Yellowknife","NT",8170,-41,25,8,9,1,12,14,-26,-23,-17,-5,4,13,17,14,7,-2,-14,-22,62.48,-114.35]
[265,"Alert","NU",13030,-43,13,4,5,-10,7,12,-32,-33,-33,-25,-12,-1,3,1,-8,-19,-26,-30,82.48,-62.25]
[266,"Arctic Bay","NU",11900,-42,14,7,6,-7,7,13,-31,-32,-29,-20,-8,3,6,4,-2,-12,-24,-31,73.03,-85.17]
[267,"Arviat","NU",9850,-40,22,7,9,-3,24,18,-30,-28,-23,-14,-4,4,11,11,4,-4,-16,-25,61.12,-94.05]
[268,"Baker Lake","NU",10700,-42,23,7,7,-5,24,17,-32,-31,-26,-17,-6,5,11,10,3,-7,-20,-27,64.319999999999993,-96.02]
[269,"Eureka","NU",13500,-47,12,4,5,-10,8,18,-37,-38,-37,-27,-10,3,6,3,-6,-21,-30,-34,79.9833,-85.95]
[270,"Igluligaarjuk / Chesterfield Inl","NU",10500,-40,20,7,8,-4,24,17,-32,-31,-25,-16,-6,4,11,9,3,-5,-17,-25,63.33,-90.7]
[271,"Iqaluit","NU",9980,-40,17,6,7,-3,15,12,-27,-28,-24,-14,-4,4,8,7,3,-4,-12,-21,63.73,-68.5]
[272,"Iqaluktuuttiaq / Cambridge Bay","NU",11670,-41,18,6,7,-7,22,20,-33,-33,-29,-21,-9,3,9,7,0,-11,-23,-29,69.12,-105.03]
[273,"Isachsen","NU",13600,-46,12,6,6,-11,14,16,-35,-37,-35,-27,-13,-1,3,0,-9,-20,-29,-34,78.78,-103.53]
[274,"Kangiqiniq / Rankin Inlet","NU",10500,-41,21,6,8,-4,24,19,-31,-30,-25,-16,-6,4,10,10,4,-5,-17,-26,62.82,-92.08]
[275,"Kanngiqtugaapik / Clyde River","NU",11300,-40,14,7,6,-6,15,13,-28,-30,-27,-19,-9,1,4,4,0,-8,-17,-25,70.45,-68.569999999999993]
[276,"Kugluktuk / Coppermine","NU",10300,-41,23,7,9,-4,19,14,-28,-28,-25,-17,-6,5,11,9,3,-7,-19,-25,67.83,-115.08]
[277,"Nottingham Island","NU",10000,-37,16,6,8,-3,15,15,-25,-26,-22,-14,-6,2,7,6,2,-4,-12,-20,63.1,-78]
[278,"Resolute","NU",12360,-42,11,4,6,-8,20,21,-32,-33,-30,-22,-10,0,4,2,-4,-14,-23,-29,74.680000000000007,-94.9]
[279,"Resolution Island","NU",9000,-32,12,4,7,-1,39,28,-20,-21,-17,-10,-4,1,6,5,1,-3,-7,-13,61.3,-64.883300000000006]
[280,"Salliq / Coral Harbour","NU",10720,-41,20,7,8,-4,19,17,-30,-31,-25,-16,-7,3,10,8,2,-6,-17,-25,64.13,-83.17]
[281,"Ailsa Craig","ON",3840,-17,30,12,15,10,19,11,-6,-5,0,7,14,19,21,20,16,10,3,-3,43.13,-81.55]
[282,"Ajax","ON",3820,-20,30,10,15,10,17,10,-5,-4,0,6,12,17,20,20,15,9,4,-2,43.85,-79.03]
[283,"Alexandria","ON",4600,-24,30,11,15,9,12,8,-11,-11,-4,4,12,18,20,19,15,9,0,-8,45.32,-74.63]
[284,"Alliston","ON",4200,-23,29,12,15,9,12,10,-7,-6,-1,6,13,18,21,20,15,9,3,-3,44.15,-79.87]
[285,"Almonte","ON",4620,-26,30,12,15,9,13,9,-11,-8,-3,4,13,17,20,18,14,6,1,-8,45.23,-76.2]
[286,"Armstrong","ON",6500,-37,28,13,13,9,8,9,-18,-16,-8,0,7,14,17,15,11,3,-6,-13,50.3,-89.03]
[287,"Arnprior","ON",4680,-27,30,12,15,5,14,10,-12,-10,-3,5,13,18,21,19,14,8,1,-7,45.43,-76.349999999999994]
[288,"Atikokan","ON",5750,-33,29,12,14,9,7,7,-15,-12,-5,3,10,16,19,17,13,5,-3,-11,48.75,-91.62]
[289,"Attawapiskat","ON",7100,-37,28,13,13,6,13,13,-22,-19,-10,-3,5,12,15,14,9,3,-5,-17,52.93,-82.43]
[290,"Aurora","ON",4210,-21,30,10,15,9,14,10,-8,-7,-2,6,13,18,20,19,15,8,2,-4,44,-79.47]
[291,"Bancroft","ON",4740,-28,29,14,15,8,7,6,-10,-8,-3,4,11,16,18,17,13,6,0,-6,45.05,-77.849999999999994]
[292,"Barrie","ON",4380,-24,29,11,15,9,13,8,-8,-7,-2,5,12,17,20,19,15,9,2,-4,44.4,-79.67]
[293,"Barriefield","ON",3990,-22,28,9,16,10,19,13,-7,-6,-1,7,13,18,21,20,16,9,3,-3,44.23,-76.47]
[294,"Beaverton","ON",4300,-24,30,8,15,9,17,15,-9,-7,-3,5,12,18,20,20,16,9,3,-3,44.43,-79.150000000000006]
[295,"Belleville","ON",3910,-22,29,10,15,10,17,12,-7,-6,-1,7,14,19,22,21,16,9,3,-3,44.166699999999999,-77.383300000000006]
[296,"Belmont","ON",3840,-17,30,10,16,10,19,11,-7,-7,0,6,13,18,21,20,16,9,3,-3,42.88,-81.08]
[297,"Bracebridge","ON",4800,-26,29,12,15,8,15,12,-9,-9,-2,4,13,16,20,18,13,7,1,-6,45.03,-79.3]
[298,"Bradford","ON",4280,-23,30,12,15,9,12,10,-7,-6,-1,6,12,17,20,19,15,8,2,-4,44.12,-79.569999999999993]
[299,"Brampton","ON",4100,-19,30,11,15,9,18,13,-6,-6,-1,7,14,19,22,20,15,9,4,-3,43.68,-79.77]
[300,"Brantford","ON",3900,-18,30,11,15,10,15,12,-6,-5,0,7,14,19,21,20,16,9,4,-3,43.13,-80.27]
[301,"Brighton","ON",4000,-21,29,10,15,10,17,12,-6,-4,0,6,11,17,20,20,16,9,4,-1,44.03,-77.73]
[302,"Brockville","ON",4060,-23,29,10,15,10,18,13,-8,-7,-1,6,13,18,21,20,15,9,3,-4,44.59,-75.680000000000007]
[303,"Burk's Falls","ON",5020,-26,29,13,14,8,12,10,-13,-10,-5,3,11,15,17,17,12,6,0,-8,45.62,-79.400000000000006]
[304,"Burlington","ON",3740,-17,31,7,14,10,15,11,-3,-2,1,7,13,19,22,21,18,11,6,0,43.32,-79.8]
[305,"Cambridge","ON",4100,-18,29,12,15,10,15,10,-7,-6,-1,6,13,18,20,19,15,9,3,-4,43.38,-80.319999999999993]
[306,"Campbellford","ON",4280,-23,30,12,15,9,13,9,-5,-6,-1,7,14,19,21,20,15,9,2,-5,44.3,-77.8]
[307,"Cannington","ON",4310,-24,30,11,15,9,13,9,-7,-7,-2,5,12,18,20,19,15,8,2,-5,44.35,-79.03]
[308,"Carleton Place","ON",4600,-25,30,13,15,9,13,9,-10,-8,-2,6,13,18,21,19,14,8,1,-6,45.13,-76.150000000000006]
[309,"Cavan","ON",4400,-23,30,12,15,9,13,9,-8,-6,-2,6,12,17,19,19,15,8,2,-3,44.2,-78.47]
[310,"Centralia","ON",3800,-17,30,11,15,10,19,11,-6,-6,0,6,13,18,20,19,15,9,3,-3,43.28,-81.47]
[311,"CFB Borden","ON",4300,-23,29,13,15,8,12,10,-5,-6,-2,6,13,17,20,19,14,8,2,-5,44.27,-79.88]
[312,"Chapleau","ON",5900,-35,27,12,13,6,10,12,-16,-13,-7,1,9,14,17,16,11,4,-4,-12,47.83,-83.4]
[313,"Chatham","ON",3470,-16,31,10,16,11,17,13,-4,-2,2,8,15,20,22,21,18,11,5,-1,42.4,-82.18]
[314,"Chesley","ON",4320,-19,29,12,14,9,17,10,-7,-7,-2,5,11,16,19,18,14,8,2,-4,44.28,-81.08]
[315,"Clinton","ON",4150,-17,29,12,15,9,19,12,-6,-6,-1,6,13,17,20,19,15,9,3,-3,43.62,-81.53]
[316,"Coboconk","ON",4500,-25,30,11,15,8,13,9,-10,-9,-3,5,13,17,20,19,14,8,1,-6,44.65,-78.8]
[317,"Cobourg","ON",3980,-21,29,7,15,10,15,8,-6,-4,0,6,11,17,20,20,16,9,4,-1,43.97,-78.17]
[318,"Cochrane","ON",6200,-34,29,13,12,6,12,11,-18,-16,-9,1,9,14,17,15,10,4,-4,-15,49.07,-81.02]
[319,"Colborne","ON",3980,-21,29,7,15,10,16,10,-6,-4,0,6,11,17,20,20,16,9,4,-1,44,-77.88]
[320,"Collingwood","ON",4180,-21,29,8,15,8,15,10,-5,-5,-1,6,11,18,21,20,16,10,4,-2,44.48,-80.22]
[321,"Cornwall","ON",4250,-23,30,10,15,9,17,13,-9,-7,-1,6,14,19,22,20,16,9,3,-5,45.03,-74.73]
[322,"Corunna","ON",3600,-16,31,11,16,10,18,13,-5,-4,1,8,14,19,22,21,17,11,4,-2,42.88,-82.43]
[323,"Deep River","ON",4900,-29,30,12,13,8,11,9,-12,-10,-3,5,13,17,20,19,14,7,0,-8,46.1,-77.5]
[324,"Deseronto","ON",4070,-22,29,12,15,10,18,13,-8,-6,-1,6,13,18,20,20,15,9,3,-3,44.2,-77.05]
[325,"Dorchester","ON",3900,-18,30,10,16,10,19,11,-5,-5,0,7,13,18,21,20,16,9,4,-2,42.98,-81.069999999999993]
[326,"Dorion","ON",5950,-33,28,13,13,6,12,10,-18,-14,-7,1,9,13,16,15,10,5,-3,-13,48.78,-88.53]
[327,"Dresden","ON",3750,-16,31,11,16,11,17,13,-6,-5,1,7,14,19,21,20,16,10,4,-2,42.58,-82.18]
[328,"Dryden","ON",5850,-34,28,11,14,6,12,12,-23,-19,-12,-3,5,10,13,12,6,1,-9,-19,49.78,-92.75]
[329,"Dundalk","ON",4700,-22,29,11,14,8,15,10,-9,-8,-4,4,11,15,18,17,13,7,1,-5,44.170299999999997,-80.393600000000006]
[330,"Dunnville","ON",3660,-15,30,11,16,10,18,11,-6,-5,0,6,13,18,21,20,16,10,4,-2,42.9,-79.62]
[331,"Durham","ON",4340,-20,29,11,14,9,17,10,-8,-7,-2,5,12,17,19,19,14,8,2,-4,44.17,-80.819999999999993]
[332,"Dutton","ON",3700,-16,31,12,16,10,17,11,-6,-4,1,7,13,19,21,20,16,11,4,-2,42.67,-81.5]
[333,"Earlton","ON",5730,-33,29,12,14,6,14,13,-16,-12,-7,3,10,15,18,16,12,5,-3,-13,47.72,-79.819999999999993]
[334,"Edison","ON",5740,-34,28,14,14,6,12,12,-20,-16,-8,1,10,15,18,16,10,4,-5,-16,49.8,-93.55]
[335,"Elliot Lake","ON",4950,-26,29,11,12,7,11,11,-11,-10,-4,4,11,17,19,18,13,6,-1,-7,46.381100000000004,-82.657200000000003]
[336,"Elmvale","ON",4200,-24,29,12,15,8,12,7,-7,-7,-2,5,12,17,20,19,14,8,2,-4,44.58,-79.87]
[337,"Embro","ON",3950,-19,30,12,15,10,17,11,-6,-5,0,6,13,18,20,20,15,9,3,-3,43.15,-80.900000000000006]
[338,"Englehart","ON",5800,-33,29,12,14,6,14,13,-16,-12,-7,3,10,15,18,16,12,5,-3,-13,47.82,-79.87]
[339,"Espanola","ON",4920,-25,29,14,12,8,16,13,-12,-11,-5,4,11,16,19,17,12,6,0,-9,46.25,-81.77]
[340,"Etobicoke","ON",3800,-20,31,10,16,10,18,12,-5,-4,0,7,13,19,22,20,16,10,4,-2,43.7,-79.569999999999993]
[341,"Exeter","ON",3900,-17,30,11,15,10,19,12,-6,-6,0,6,13,18,20,19,15,9,3,-3,43.35,-81.48]
[342,"Fenelon Falls","ON",4440,-25,30,12,15,9,13,9,-9,-7,-2,5,12,18,20,18,14,9,2,-4,44.53,-78.75]
[343,"Fergus","ON",4300,-20,29,10,15,9,16,10,-8,-7,-2,5,12,17,20,19,14,8,2,-5,43.7,-80.37]
[344,"Forest","ON",3740,-16,31,11,14,10,19,12,-4,-4,1,7,13,19,21,20,16,10,4,-2,43.1,-82]
[345,"Fort Erie","ON",3650,-15,30,10,16,10,24,15,-5,-4,0,6,12,18,21,20,16,10,5,-1,42.9,-78.930000000000007]
[346,"Fort Erie (Ridgeway)","ON",3600,-15,30,10,16,10,24,15,-5,-4,0,6,12,18,21,20,16,10,5,-1,42.88,-79.05]
[347,"Fort Frances","ON",5440,-33,29,12,14,7,10,9,-16,-12,-4,4,12,17,20,18,12,6,-3,-12,48.61,-93.39]
[348,"Gananoque","ON",4010,-22,28,9,16,10,18,13,-7,-6,-1,7,13,18,21,20,16,9,3,-3,44.33,-76.17]
[349,"Geraldton","ON",6450,-36,28,12,13,5,11,11,-19,-15,-9,1,9,14,17,16,10,3,-6,-14,49.73,-86.95]
[350,"Glencoe","ON",3680,-16,31,12,16,11,17,10,-6,-4,1,7,13,19,21,20,16,11,4,-2,42.75,-81.72]
[351,"Goderich","ON",4000,-16,29,9,15,9,21,12,-4,-4,0,6,12,17,20,19,16,10,5,-1,43.75,-81.72]
[352,"Gore Bay","ON",4700,-24,28,9,14,8,18,14,-9,-8,-4,4,11,16,19,19,15,8,2,-4,45.92,-82.47]
[353,"Graham","ON",5940,-35,29,13,14,6,8,7,-19,-15,-8,1,10,15,18,16,10,4,-5,-15,49.25,-90.57]
[354,"Gravenhurst (Muskoka Airport)","ON",4760,-26,29,12,15,8,15,12,-10,-9,-3,4,12,16,19,18,13,7,1,-7,44.92,-79.37]
[355,"Grimsby","ON",3520,-16,30,11,15,10,21,13,-4,-4,1,7,14,19,22,21,17,10,5,-1,43.2,-79.569999999999993]
[356,"Guelph","ON",4270,-19,29,12,15,9,15,10,-8,-7,-1,6,12,17,20,19,14,8,2,-4,43.55,-80.25]
[357,"Guthrie","ON",4300,-24,29,11,15,9,13,8,-8,-7,-2,5,12,17,20,19,15,9,2,-4,44.47,-79.55]
[358,"Haileybury","ON",5600,-32,30,10,13,7,13,12,-15,-12,-6,2,11,17,20,18,13,7,-1,-10,47.45,-79.63]
[359,"Haldimand (Caledonia)","ON",3750,-18,30,12,15,9,20,13,-5,-4,0,7,13,19,21,20,16,10,3,-2,43.07,-79.930000000000007]
[360,"Haldimand (Hagersville)","ON",3760,-17,30,11,15,10,18,11,-4,-4,1,7,14,19,21,20,16,10,4,-2,42.97,-80.05]
[361,"Haliburton","ON",4840,-27,29,12,15,8,11,10,-11,-9,-4,4,12,16,19,18,13,7,1,-7,45.05,-78.52]
[362,"Halton Hills (Georgetown)","ON",4200,-19,30,14,15,9,18,12,-7,-6,-1,6,12,17,20,19,14,8,2,-3,43.65,-79.92]
[363,"Hamilton","ON",3460,-17,31,10,14,10,17,13,-5,-4,0,7,13,19,22,21,16,10,4,-2,43.25,-79.86]
[364,"Hanover","ON",4300,-19,29,13,14,9,17,10,-7,-7,-2,5,12,17,19,19,14,8,2,-4,44.15,-81.03]
[365,"Hastings","ON",4280,-24,30,12,15,9,13,9,-8,-7,-1,6,12,18,20,20,14,9,2,-4,44.3,-77.95]
[366,"Hawkesbury","ON",4610,-25,30,12,15,9,12,8,-11,-9,-3,5,13,18,20,19,14,7,0,-8,45.6,-74.62]
[367,"Hearst","ON",6450,-35,29,13,12,5,10,10,-19,-15,-9,0,8,15,17,16,12,4,-5,-12,49.68,-83.67]
[368,"Honey Harbour","ON",4300,-24,29,10,15,8,9,6,-8,-7,-2,5,12,18,21,20,16,9,3,-3,44.87,-79.819999999999993]
[369,"Hornepayne","ON",6340,-37,28,15,13,5,9,9,-20,-16,-9,0,9,13,16,14,9,4,-4,-15,49.22,-84.78]
[370,"Huntsville","ON",4850,-26,29,11,14,8,15,12,-10,-9,-3,5,12,17,19,18,14,8,1,-6,45.33,-79.22]
[371,"Ingersoll","ON",3920,-18,30,10,15,10,19,11,-6,-5,0,6,13,18,21,20,16,9,3,-3,43.03,-80.88]
[372,"Iroquois Falls","ON",6100,-33,29,14,12,5,12,11,-18,-16,-9,1,9,15,17,16,10,4,-4,-14,48.77,-80.680000000000007]
[373,"Jellicoe","ON",6400,-36,28,12,13,5,11,11,-19,-15,-9,1,9,14,17,16,10,3,-6,-14,49.68,-87.52]
[374,"Kapuskasing","ON",6250,-34,29,12,12,5,13,11,-18,-15,-8,1,9,15,17,16,11,4,-4,-13,49.42,-82.43]
[375,"Kemptville","ON",4540,-25,30,12,15,9,11,8,-10,-9,-3,6,13,18,20,19,14,8,1,-7,45.02,-75.64]
[376,"Kenora","ON",5630,-33,28,9,14,6,13,13,-16,-12,-5,4,11,17,20,19,13,5,-5,-13,49.82,-94.43]
[377,"Killaloe","ON",4960,-28,30,14,13,8,12,10,-12,-10,-4,-5,12,17,19,18,13,8,1,-8,45.55,-77.42]
[378,"Kincardine","ON",3890,-17,28,10,14,10,21,12,-5,-4,0,5,12,18,19,19,15,10,3,-2,44.18,-81.63]
[379,"Kingston","ON",4000,-22,28,9,16,10,19,13,-7,-6,-1,7,13,18,21,20,16,9,3,-3,44.23,-76.48]
[380,"Kinmount","ON",4600,-26,29,13,15,9,13,9,-10,-9,-3,5,12,16,19,18,13,7,1,-6,44.78,-78.650000000000006]
[381,"Kirkland Lake","ON",6000,-33,29,12,14,6,13,12,-17,-15,-8,1,10,15,18,16,11,5,-4,-13,48.15,-80.03]
[382,"Kitchener","ON",4200,-19,29,12,15,9,15,10,-7,-6,-1,6,13,17,20,19,14,8,2,-4,43.45,-80.48]
[383,"Kitchenuhmaykoosib","ON",7450,-38,26,11,12,3,14,15,-22,-20,-12,-3,6,13,16,15,9,2,-8,-17,53.83,-90]
[384,"Lakefield","ON",4330,-24,30,12,15,9,13,9,-8,-7,-1,6,13,18,20,19,15,8,2,-5,44.43,-78.27]
[385,"Lansdowne House","ON",7150,-38,28,10,13,5,14,14,-21,-18,-11,-1,7,14,17,16,10,3,-7,-16,52.23,-87.88]
[386,"Leamington","ON",3400,-15,31,9,16,11,15,9,-5,-4,1,7,14,19,22,21,17,11,5,-1,42.08,-82.57]
[387,"Lindsay","ON",4320,-24,30,12,15,9,12,10,-9,-7,-2,6,13,17,20,19,14,8,2,-5,44.35,-78.73]
[388,"Lion's Head","ON",4300,-19,27,10,15,8,19,12,-6,-6,-2,5,11,16,19,18,15,9,3,-3,44.98,-81.25]
[389,"Listowel","ON",4300,-19,29,11,15,9,17,11,-6,-7,-1,5,12,17,19,19,14,8,2,-4,43.73,-80.95]
[390,"London","ON",3900,-18,30,10,16,10,19,11,-5,-5,0,7,13,18,21,20,16,9,4,-2,42.98,-81.23]
[391,"Lucan","ON",3900,-17,30,12,15,10,19,11,-6,-5,0,7,14,19,21,20,16,10,3,-3,43.18,-81.400000000000006]
[392,"Maitland","ON",4080,-23,29,10,15,10,18,13,-8,-7,-1,6,13,18,21,20,15,9,3,-4,44.63,-75.62]
[393,"Markdale","ON",4500,-20,29,11,14,8,17,10,-8,-7,-3,4,11,17,18,18,13,8,1,-5,44.32,-80.650000000000006]
[394,"Markham","ON",4000,-21,31,11,16,10,15,11,-6,-5,-1,6,13,19,21,20,16,9,3,-3,43.87,-79.27]
[395,"Martin","ON",5900,-35,29,13,14,6,8,7,-19,-15,-8,1,10,15,18,16,10,4,-5,-15,49.25,-91.13]
[396,"Matheson","ON",6080,-33,29,13,12,6,12,11,-17,-15,-8,1,10,15,18,16,11,5,-4,-13,48.53,-80.47]
[397,"Mattawa","ON",5050,-29,30,12,13,8,12,10,-12,-12,-5,2,11,16,19,18,13,8,0,-8,46.32,-78.7]
[398,"Midland","ON",4200,-24,29,10,15,8,9,6,-9,-7,-2,6,13,18,21,20,15,9,3,-4,44.75,-79.88]
[399,"Milton","ON",3920,-18,30,12,15,10,15,11,-7,-6,-1,6,12,17,20,19,15,9,3,-3,43.52,-79.88]
[400,"Milverton","ON",4200,-19,29,11,15,9,17,11,-6,-7,-1,5,12,17,19,19,14,8,2,-4,43.57,-80.92]
[401,"Minden","ON",4640,-27,29,14,15,8,14,10,-10,-9,-3,5,12,16,19,18,13,7,1,-6,44.92,-78.73]
[402,"Mississauga","ON",3880,-18,30,9,15,10,18,12,-5,-4,0,6,12,17,21,20,16,10,5,-1,43.58,-79.650000000000006]
[403,"Mississauga (LBP Int'l Airport)","ON",3890,-20,31,10,16,10,18,12,-5,-4,0,7,13,19,22,20,16,10,4,-2,43.68,-79.61]
[404,"Mississauga (Port Credit)","ON",3780,-18,29,9,15,10,23,12,-5,-4,0,6,12,17,21,20,16,10,5,-1,43.55,-79.58]
[405,"Mitchell","ON",4100,-18,29,12,15,9,17,11,-7,-7,-1,6,13,17,20,19,15,8,2,-4,43.47,-81.2]
[406,"Moosonee","ON",6800,-36,28,12,14,5,11,11,-20,-17,-11,-2,7,13,16,16,11,5,-4,-13,51.32,-80.72]
[407,"Morrisburg","ON",4370,-23,30,12,15,9,18,13,-10,-9,-2,6,13,18,20,19,14,8,2,-6,44.9,-75.180000000000007]
[408,"Mount Forest","ON",4700,-21,28,10,14,9,16,18,-7,-7,-2,5,11,17,19,18,14,8,2,-4,43.98,-80.73]
[409,"Nakina","ON",6500,-36,28,12,13,5,11,11,-19,-15,-9,1,9,14,17,16,10,3,-6,-14,50.17,-86.7]
[410,"Nanticoke (Jarvis)","ON",3700,-17,30,11,15,10,17,11,-6,-5,0,6,13,18,21,20,16,9,4,-3,42.88,-80.099999999999994]
[411,"Nanticoke (Port Dover)","ON",3600,-15,30,10,16,10,17,11,-6,-5,0,6,13,18,21,20,16,10,4,-2,42.78,-80.2]
[412,"Napanee","ON",4140,-22,29,12,15,9,18,13,-8,-6,-1,6,13,18,20,20,15,9,3,-3,44.25,-76.95]
[413,"New Liskeard","ON",5570,-32,30,13,13,7,13,12,-16,-15,-7,1,10,16,19,16,11,6,-2,-12,47.5,-79.67]
[414,"Newcastle","ON",3990,-20,30,11,15,9,15,8,-6,-5,0,6,12,17,20,19,15,8,3,-3,43.92,-78.58]
[415,"Newcastle (Bowmanville)","ON",4000,-20,30,11,15,10,15,8,-6,-5,0,6,12,17,20,19,15,8,3,-3,43.91,-78.680000000000007]
[416,"Newmarket","ON",4260,-22,30,11,15,9,13,10,-7,-6,-1,6,12,17,20,19,15,8,2,-4,44.05,-79.47]
[417,"Niagara Falls","ON",3600,-16,30,10,15,10,21,13,-4,-4,1,7,14,19,22,21,17,11,5,-1,43.1,-79.069999999999993]
[418,"North Bay","ON",5150,-28,28,9,14,7,14,11,-12,-10,-5,4,11,16,19,18,13,6,-1,-8,46.32,-79.47]
[419,"North York","ON",3760,-20,31,12,16,10,18,13,-7,-6,-1,6,13,18,21,20,15,9,3,-3,43.77,-79.42]
[420,"Norwood","ON",4320,-24,30,12,15,9,13,9,-9,-9,-2,5,13,17,20,19,14,8,2,-6,44.38,-77.98]
[421,"Oakville","ON",3760,-18,30,11,15,10,23,12,-5,-4,0,6,12,18,21,20,16,9,4,-2,43.45,-79.680000000000007]
[422,"Orangeville","ON",4450,-21,29,12,15,8,14,10,-8,-7,-2,5,12,17,19,18,14,8,2,-5,43.92,-80.099999999999994]
[423,"Orillia","ON",4260,-25,29,10,15,8,14,10,-8,-8,-2,6,13,17,21,19,15,8,2,-5,44.62,-79.42]
[424,"Oshawa","ON",3860,-19,30,11,15,10,15,9,-6,-5,1,7,14,18,21,20,16,9,4,-3,43.9,-78.849999999999994]
[425,"Ottawa (Barrhaven)","ON",4500,-25,30,10,15,9,15,10,-10,-8,-2,6,13,19,21,20,15,8,2,-6,45.28,-75.760000000000005]
[426,"Ottawa (city hall)","ON",4440,-25,30,11,15,10,12,9,-10,-9,-2,6,14,18,21,20,15,8,2,-7,45.42,-75.69]
[427,"Ottawa (Kanata)","ON",4520,-25,30,10,15,9,15,10,-11,-10,-3,6,13,18,21,19,15,11,1,-7,45.31,-75.91]
[428,"Ottawa (M-C Int'l Airport)","ON",4500,-25,30,10,15,9,15,10,-10,-8,-2,6,13,19,21,20,15,8,2,-6,45.32,-75.67]
[429,"Ottawa (Orleans)","ON",4500,-26,30,11,15,8,14,12,-11,-10,-3,5,13,18,21,19,14,8,1,-7,45.48,-75.52]
[430,"Owen Sound","ON",4030,-19,29,10,14,9,17,10,-6,-6,-1,5,11,16,20,19,15,10,3,-2,44.57,-80.930000000000007]
[431,"Pagwa River","ON",6500,-35,28,13,13,5,10,10,-19,-15,-9,0,8,15,17,16,12,4,-5,-12,50.02,-85.22]
[432,"Paris","ON",4000,-18,30,11,15,10,15,12,-6,-5,0,7,14,19,21,20,16,9,4,-3,43.2,-80.38]
[433,"Parkhill","ON",3800,-16,31,11,14,10,19,11,-5,-4,1,7,13,19,21,20,16,10,4,-2,43.15,-81.680000000000007]
[434,"Parry Sound","ON",4640,-24,28,9,14,8,10,10,-9,-7,-2,6,12,16,20,19,15,8,2,-5,45.35,-80.03]
[435,"Pelham (Fonthill)","ON",3690,-15,30,9,15,11,13,8,-5,-4,1,7,14,19,21,21,17,10,4,-2,43.03,-79.28]
[436,"Pembroke","ON",4980,-28,30,13,15,8,11,9,-12,-10,-4,5,12,17,19,18,14,7,0,-8,45.82,-77.12]
[437,"Penetanguishene","ON",4200,-24,29,10,15,9,9,6,-9,-7,-2,6,13,18,21,20,15,9,3,-4,44.78,-79.92]
[438,"Perth","ON",4540,-25,30,12,15,9,11,8,-10,-8,-2,6,14,18,21,20,15,8,2,-6,44.9,-76.25]
[439,"Petawawa","ON",4980,-29,30,13,15,8,11,9,-12,-10,-4,5,12,17,19,18,14,7,0,-8,45.9,-77.33]
[440,"Peterborough","ON",4400,-23,30,12,15,9,13,9,-8,-6,-2,6,12,17,19,19,15,8,2,-3,44.3,-78.319999999999993]
[441,"Petrolia","ON",3640,-16,31,12,16,10,19,12,-5,-4,1,7,14,19,21,21,17,10,4,-2,42.87,-82.15]
[442,"Pickering (Dunbarton)","ON",3800,-19,30,9,15,10,17,10,-5,-4,0,6,12,17,20,20,15,9,4,-2,43.82,-79.099999999999994]
[443,"Picton","ON",3980,-21,29,9,15,10,19,13,-7,-6,-1,6,13,17,21,20,16,10,4,-3,44,-77.13]
[444,"Plattsville","ON",4150,-19,29,11,15,10,15,11,-7,-6,-1,6,13,18,20,19,15,9,2,-4,43.3,-80.62]
[445,"Point Alexander","ON",4960,-29,30,12,13,8,11,9,-12,-10,-4,4,13,18,20,18,14,8,0,-6,46.13,-77.569999999999993]
[446,"Port Burwell","ON",3800,-15,30,10,16,10,19,11,-6,-5,0,6,12,17,20,19,16,9,4,-2,42.65,-80.819999999999993]
[447,"Port Colborne","ON",3600,-15,30,5,16,10,27,18,-3,-3,0,5,11,18,21,21,17,11,5,0,42.9,-79.23]
[448,"Port Elgin","ON",4100,-17,28,9,14,9,21,12,-6,-7,-1,5,11,16,19,19,15,9,4,-3,44.43,-81.400000000000006]
[449,"Port Hope","ON",3970,-21,29,9,15,10,15,8,-6,-5,0,6,12,16,20,20,16,9,4,-3,43.95,-78.3]
[450,"Port Perry","ON",4260,-22,30,13,15,9,15,11,-8,-7,-2,7,12,17,20,19,14,8,2,-4,44.1,-78.95]
[451,"Port Stanley","ON",3850,-15,31,10,16,10,19,11,-6,-5,0,6,12,17,20,19,16,9,4,-2,42.67,-81.22]
[452,"Prescott","ON",4120,-23,29,10,15,10,18,13,-8,-6,-1,6,13,19,21,20,16,10,3,-3,44.72,-75.52]
[453,"Princeton","ON",4000,-18,30,12,15,10,15,12,-6,-5,0,6,13,18,20,20,15,9,3,-3,43.17,-80.53]
[454,"Raith","ON",5900,-34,28,16,14,6,8,8,-19,-15,-9,1,9,13,16,14,9,4,-5,-15,48.83,-89.93]
[455,"Rayside-Balfour (Chelmsford)","ON",5200,-28,29,10,12,8,17,13,-12,-11,-4,4,12,17,20,19,13,8,0,-9,46.58,-81.2]
[456,"Red Lake","ON",6220,-35,28,10,13,5,9,11,-19,-15,-8,3,11,15,19,17,10,4,-7,-17,51.05,-93.82]
[457,"Renfrew","ON",4900,-27,30,13,15,9,12,9,-12,-10,-4,5,12,17,20,19,13,7,0,-8,45.47,-76.680000000000007]
[458,"Richmond Hill","ON",4000,-21,31,11,16,10,15,11,-7,-6,-1,7,13,18,21,20,15,9,3,-3,43.87,-79.45]
[459,"Rockland","ON",4600,-26,30,12,15,10,11,9,-13,-9,-3,5,13,18,21,19,14,8,1,-8,45.55,-75.290000000000006]
[460,"Sarnia","ON",3750,-16,31,11,16,10,19,12,-5,-4,1,6,13,18,21,20,16,10,4,-2,42.97,-82.38]
[461,"Sault Ste. Marie","ON",4960,-25,29,11,14,8,14,11,-10,-9,-4,4,10,15,18,18,14,7,1,-5,46.52,-84.33]
[462,"Scarborough","ON",3800,-20,31,10,16,10,17,13,-6,-5,0,7,13,18,21,20,16,9,3,-3,43.78,-79.25]
[463,"Schreiber","ON",5960,-34,27,10,13,5,11,10,-15,-13,-7,1,8,12,15,15,10,5,-3,-11,48.8,-87.25]
[464,"Seaforth","ON",4100,-17,30,12,15,9,17,11,-6,-6,-1,6,13,17,20,19,15,9,3,-3,43.55,-81.400000000000006]
[465,"Shelburne","ON",4700,-22,29,11,15,8,14,10,-8,-8,-3,5,12,16,19,18,13,7,1,-5,44.0764,-80.204400000000007]
[466,"Simcoe","ON",3700,-17,30,11,16,10,17,11,-6,-5,0,6,13,18,21,20,16,9,4,-3,42.83,-80.3]
[467,"Sioux Lookout","ON",5950,-34,28,10,14,6,10,10,-17,-14,-7,3,10,16,19,18,12,4,-5,-14,50.07,-91.98]
[468,"Smiths Falls","ON",4540,-25,30,12,15,9,11,8,-10,-8,-2,6,14,18,21,20,15,8,2,-6,44.9,-76.02]
[469,"Smithville","ON",3650,-16,30,11,15,10,21,13,-4,-4,1,7,14,19,22,21,17,10,5,-1,43.1,-79.55]
[470,"Smooth Rock Falls","ON",6250,-34,29,12,12,5,13,11,-18,-15,-8,1,9,15,17,16,11,4,-4,-13,49.28,-81.63]
[471,"South River","ON",5090,-27,29,12,14,8,12,10,-12,-11,-4,4,11,15,19,17,12,6,-1,-8,45.83,-79.38]
[472,"Southampton","ON",4100,-17,28,9,14,9,21,12,-6,-7,-1,5,11,16,19,19,15,9,4,-3,44.48,-81.38]
[473,"St. Catharines","ON",3540,-16,30,11,15,10,21,13,-4,-4,1,7,14,19,22,21,17,10,5,-1,43.17,-79.25]
[474,"St. Mary's","ON",4000,-18,30,11,15,10,15,11,-7,-6,-1,6,13,17,20,19,15,9,3,-3,43.25,-81.13]
[475,"St. Thomas","ON",3780,-16,31,12,16,10,19,11,-5,-4,1,7,14,19,21,20,16,10,4,-2,42.78,-81.2]
[476,"Stirling","ON",4220,-23,30,13,15,9,13,9,-8,-7,-2,7,13,17,21,19,15,8,2,-5,44.3,-77.55]
[477,"Stratford","ON",4050,-18,29,11,15,9,15,11,-7,-6,-1,6,13,17,20,19,15,9,3,-3,43.37,-80.95]
[478,"Strathroy","ON",3780,-17,31,11,16,10,19,11,-6,-5,1,7,14,19,21,20,16,10,4,-3,42.95,-81.63]
[479,"Sturgeon Falls","ON",5200,-28,29,12,12,9,14,11,-16,-10,-5,4,10,15,19,18,13,7,0,-8,46.37,-79.92]
[480,"Sudbury","ON",5180,-28,29,10,12,8,17,13,-13,-11,-5,4,11,16,19,18,13,6,-1,-8,46.5,-81]
[481,"Sundridge","ON",5080,-27,29,12,14,8,12,10,-12,-11,-4,4,11,15,19,17,12,6,-1,-8,45.77,-79.400000000000006]
[482,"Tavistock","ON",4100,-19,29,11,15,10,15,11,-7,-6,-1,6,13,17,20,19,15,9,3,-3,43.32,-80.83]
[483,"Temagami","ON",5420,-30,30,10,13,8,11,10,-16,-15,-7,1,10,16,19,16,11,6,-2,-12,47.07,-79.78]
[484,"Thamesford","ON",3950,-19,30,10,15,10,19,11,-5,-5,0,7,13,18,21,20,16,9,4,-2,43.07,-81]
[485,"Thedford","ON",3710,-16,31,11,14,10,19,12,-4,-4,1,7,13,19,21,20,16,10,4,-2,43.15,-81.849999999999994]
[486,"Thunder Bay","ON",5650,-31,29,12,12,6,12,10,-14,-11,-5,3,9,15,18,17,12,5,-3,-10,48.4,-89.32]
[487,"Tillsonburg","ON",3840,-17,30,13,16,10,14,9,-4,-1,2,8,15,19,21,20,17,10,4,-2,42.85,-80.73]
[488,"Timmins","ON",5940,-34,29,12,12,5,12,11,-17,-14,-8,2,10,15,17,16,11,4,-4,-12,48.47,-81.33]
[489,"Timmins (Porcupine)","ON",6000,-34,29,12,12,6,12,11,-17,-14,-8,2,10,15,17,16,11,4,-4,-12,48.5,-81.17]
[490,"Toronto (city hall)","ON",3520,-18,31,7,14,10,23,12,-4,-2,1,6,12,18,21,21,18,10,5,0,43.65,-79.38]
[491,"Trenton","ON",4110,-22,29,10,15,10,17,12,-7,-6,-1,6,13,18,21,20,15,9,3,-3,44.1,-77.58]
[492,"Trout Creek","ON",5100,-27,29,9,14,8,11,10,-12,-10,-5,4,11,16,19,18,13,6,-1,-8,45.98,-79.37]
[493,"Uxbridge","ON",4240,-22,30,12,15,9,15,11,-9,-9,-3,4,12,17,19,18,14,8,2,-5,44.1,-79.12]
[494,"Vaughan (Woodbridge)","ON",4100,-20,31,12,16,10,18,13,-7,-6,-1,6,13,18,21,20,15,9,3,-3,43.78,-79.599999999999994]
[495,"Vittoria","ON",3680,-15,30,10,16,10,17,11,-6,-5,0,6,13,18,21,20,16,10,4,-2,42.77,-80.319999999999993]
[496,"Walkerton","ON",4300,-18,30,13,13,9,17,10,-7,-7,-2,5,12,17,19,19,14,8,2,-4,44.12,-81.150000000000006]
[497,"Wallaceburg","ON",3600,-16,31,11,16,11,17,13,-5,-4,1,8,14,20,22,21,17,11,4,-2,42.6,-82.38]
[498,"Waterloo","ON",4200,-19,29,12,15,9,15,10,-7,-6,-1,6,13,17,20,19,14,8,2,-4,43.47,-80.52]
[499,"Watford","ON",3740,-17,31,11,16,10,19,12,-6,-5,1,7,14,19,21,20,16,10,4,-3,42.95,-81.88]
[500,"Wawa","ON",5840,-34,26,11,14,6,10,7,-13,-11,-6,2,8,13,15,16,12,5,-2,-8,47.98,-84.78]
[501,"Welland","ON",3670,-15,30,11,15,10,13,8,-5,-4,1,7,13,19,21,21,16,10,4,-1,42.98,-79.25]
[502,"West Lorne","ON",3700,-16,31,12,16,11,17,11,-6,-4,1,7,13,19,21,20,16,11,4,-2,42.6,-81.599999999999994]
[503,"Whitby","ON",3820,-20,30,9,15,10,17,10,-5,-4,0,6,12,17,20,20,15,9,4,-2,43.87,-78.930000000000007]
[504,"Whitby (Brooklin)","ON",4010,-20,30,11,15,9,15,9,-6,-5,1,7,14,18,21,20,16,9,4,-3,43.95,-78.95]
[505,"White River","ON",6150,-39,28,14,13,6,8,9,-19,-17,-10,-1,8,14,15,15,9,4,-4,-14,48.6,-85.28]
[506,"Wiarton","ON",4300,-19,29,10,14,9,17,10,-6,-6,-2,5,11,16,19,18,15,9,3,-3,44.75,-81.150000000000006]
[507,"Windsor","ON",3400,-16,32,9,16,11,19,13,-4,-2,2,9,15,20,23,22,18,11,5,-1,42.3,-83.02]
[508,"Wingham","ON",4220,-18,30,12,15,9,17,11,-7,-7,-2,6,12,17,19,19,15,8,3,-3,43.88,-81.319999999999993]
[509,"Woodstock","ON",3910,-19,30,12,15,10,17,12,-6,-5,0,6,13,18,20,20,15,9,3,-3,43.13,-80.75]
[510,"Wyoming","ON",3700,-16,31,11,16,10,19,12,-5,-4,1,7,14,19,21,21,17,10,4,-2,42.95,-82.12]
[511,"Charlottetown","PE",4460,-20,26,9,14,8,18,14,-8,-7,-3,3,9,15,19,18,14,8,3,-3,46.2333,-63.133299999999998]
[512,"Souris","PE",4550,-19,27,6,13,8,27,19,-5,-6,-3,2,7,13,18,18,15,10,4,-1,46.35,-62.25]
[513,"Summerside","PE",4600,-20,27,8,13,8,20,16,-8,-7,-3,3,10,15,19,19,15,9,3,-4,46.4,-63.783299999999997]
[514,"Tignish","PE",4770,-20,27,6,13,9,30,19,-7,-7,-3,2,8,15,19,19,15,10,4,-2,46.95,-64.03]
[515,"Acton-Vale","QC",4620,-24,30,12,15,8,12,8,-11,-9,-3,5,13,18,20,19,14,7,1,-7,45.65,-72.569999999999993]
[516,"Alma","QC",5800,-31,28,11,14,6,13,11,-16,-14,-7,1,10,16,18,17,13,6,-1,-10,48.55,-71.650000000000006]
[517,"Amos","QC",6160,-34,28,12,13,6,13,11,-17,-15,-8,1,9,15,17,16,10,4,-4,-13,48.57,-78.12]
[518,"Ancienne-Lorette","QC",5130,-25,28,10,16,7,17,11,-12,-10,-4,4,12,17,20,18,14,7,0,-8,46.78,-71.38]
[519,"Asbestos","QC",4800,-26,29,10,14,8,11,8,-11,-9,-3,5,12,17,20,18,13,7,1,-8,45.77,-71.930000000000007]
[520,"Aylmer","QC",4520,-25,30,11,15,9,12,9,-10,-9,-2,6,14,18,21,20,15,8,2,-7,45.4,-75.83]
[521,"Baie-Comeau","QC",6020,-27,25,9,11,6,17,14,-13,-11,-5,2,8,14,17,16,12,5,-1,-8,49.22,-68.150000000000006]
[522,"Baie-Saint-Paul","QC",5280,-27,28,11,13,7,19,12,-13,-10,-4,3,10,16,18,17,12,6,-1,-9,47.44,-70.510000000000005]
[523,"Beaconsfield","QC",4440,-24,30,10,15,9,16,12,-10,-8,-2,6,13,19,21,20,16,9,2,-5,45.43,-73.87]
[524,"Beauport","QC",5100,-26,28,11,14,7,16,13,-12,-10,-4,4,11,17,20,18,13,6,0,-9,46.87,-71.180000000000007]
[525,"Bedford","QC",4420,-24,29,1,15,9,10,7,-9,-8,-1,6,13,18,21,20,15,8,2,-5,45.12,-72.98]
[526,"Beloeil","QC",4500,-24,30,11,15,9,16,11,-11,-9,-3,6,13,18,20,19,14,8,1,-6,45.57,-73.2]
[527,"Brome","QC",4730,-25,29,12,15,8,10,7,-10,-9,-3,5,12,17,19,18,13,7,1,-7,45.2,-72.569999999999993]
[528,"Brossard","QC",4420,-24,30,11,15,9,18,13,-10,-8,-2,6,13,18,21,20,15,8,2,-6,45.45,-73.47]
[529,"Buckingham","QC",4880,-26,30,12,15,9,11,9,-13,-10,-4,4,12,17,20,19,13,7,1,-8,45.58,-75.42]
[530,"Campbell's Bay","QC",4900,-28,30,13,15,9,11,9,-13,-10,-3,5,12,16,19,18,13,7,0,-7,45.73,-76.599999999999994]
[531,"Chambly","QC",4450,-24,30,11,15,9,16,11,-10,-8,-2,6,13,18,21,20,15,8,2,-6,45.45,-73.28]
[532,"Coaticook","QC",4750,-25,28,11,14,8,10,8,-10,-8,-3,5,12,17,19,18,13,7,1,-7,45.13,-71.8]
[533,"Contrecoeur","QC",4500,-25,30,11,15,9,17,11,-10,-9,-3,6,13,18,21,20,15,8,1,-6,45.85,-73.23]
[534,"Cowansville","QC",4540,-25,29,12,15,9,10,7,-10,-9,-3,5,12,17,19,18,13,7,1,-6,45.2,-72.75]
[535,"Deux-Montagnes","QC",4440,-25,29,9,15,9,17,12,-10,-9,-3,6,13,18,21,20,15,8,2,-7,45.53,-73.88]
[536,"Dolbeau","QC",6250,-32,28,12,14,6,15,12,-18,-17,-7,2,10,15,18,16,11,4,-3,-14,48.88,-72.23]
[537,"Dorval","QC",4400,-24,30,10,15,9,17,12,-10,-8,-2,6,14,19,21,20,16,9,2,-5,45.45,-73.75]
[538,"Drummondville","QC",4700,-26,30,10,15,9,13,10,-11,-9,-3,5,13,18,21,19,14,8,1,-7,45.88,-72.48]
[539,"Farnham","QC",4500,-24,29,11,15,9,10,7,-10,-9,-2,6,13,18,20,19,14,8,2,-6,45.28,-72.98]
[540,"Fort-Coulonge","QC",4950,-28,30,13,15,9,11,9,-13,-10,-3,5,12,16,19,18,13,7,0,-7,45.85,-76.73]
[541,"Gagnon","QC",7600,-34,24,10,12,4,11,14,-21,-18,-12,-4,4,11,14,12,7,0,-7,-18,51.93,-68.17]
[542,"Gaspé","QC",5500,-25,26,12,12,7,13,9,-12,-11,-5,2,8,13,17,16,12,6,0,-7,48.83,-64.48]
[543,"Gatineau","QC",4600,-25,30,11,15,9,14,12,-11,-10,-3,5,13,18,21,19,14,8,1,-7,45.5,-75.650000000000006]
[544,"Gracefield","QC",5080,-28,30,12,15,8,8,7,-13,-11,-4,5,12,17,19,18,13,7,0,-9,46.1,-76.05]
[545,"Granby","QC",4500,-25,29,10,15,8,10,7,-10,-8,-2,5,13,18,20,19,14,8,1,-6,45.4,-72.73]
[546,"Harrington-Harbour","QC",6150,-27,19,7,10,7,18,12,-13,-12,-7,-1,4,10,13,14,10,5,-1,-7,50.5,-59.48]
[547,"Havre-St-Pierre","QC",6100,-27,22,9,11,6,17,13,-14,-13,-7,0,6,12,15,14,11,5,-2,-9,50.23,-63.6]
[548,"Hemmingford","QC",4380,-24,30,12,15,9,10,7,-10,-8,-2,6,13,18,21,19,14,8,2,-6,45.05,-73.58]
[549,"Hull","QC",4550,-25,30,11,15,9,12,9,-10,-9,-2,6,14,18,21,20,15,8,2,-7,45.43,-75.73]
[550,"Iberville","QC",4450,-24,29,11,15,9,14,10,-10,-8,-2,6,13,18,21,20,15,8,2,-6,45.35,-73.23]
[551,"Inukjuak","QC",9150,-36,21,6,8,-1,20,19,-25,-26,-20,-10,-2,5,10,10,6,1,-7,-16,58.48,-78.099999999999994]
[552,"Joliette","QC",4720,-26,29,12,15,8,14,12,-12,-9,-3,5,13,18,21,19,14,7,1,-8,46.02,-73.45]
[553,"Kuujjuaq","QC",8550,-37,24,9,9,0,16,14,-25,-24,-18,-8,1,8,12,11,6,0,-8,-18,58.1,-68.400000000000006]
[554,"Kuujjuarapik","QC",7990,-36,25,8,9,1,17,14,-23,-23,-17,-7,2,7,11,12,8,3,-5,-15,55.28,-77.75]
[555,"La Pocatière","QC",5160,-24,28,10,14,8,19,12,-11,-9,-4,3,10,16,19,18,14,7,1,-6,47.37,-70.040000000000006]
[556,"Lachute","QC",4640,-26,29,11,15,9,13,8,-11,-9,-3,5,13,18,20,19,14,7,0,-8,45.65,-74.33]
[557,"Lac-Mégantic","QC",5180,-27,27,11,15,7,12,10,-11,-10,-4,3,10,15,18,17,12,6,-1,-8,45.58,-70.88]
[558,"La-Malbaie","QC",5400,-26,28,12,13,7,19,12,-13,-11,-5,3,10,15,18,17,11,6,-1,-9,47.65,-70.150000000000006]
[559,"La-Tuque","QC",5500,-30,29,13,14,7,8,8,-14,-12,-5,3,11,17,19,17,13,6,-1,-9,47.43,-72.78]
[560,"Laval","QC",4500,-24,29,11,15,9,13,11,-12,-8,-3,6,14,18,22,19,14,8,2,-7,45.58,-73.75]
[561,"Lennoxville","QC",4700,-28,29,11,14,8,10,8,-10,-7,-2,5,12,17,19,19,15,7,2,-5,45.37,-71.849999999999994]
[562,"Léry","QC",4420,-24,29,11,15,9,15,11,-11,-8,-2,6,13,18,21,20,14,8,2,-6,45.35,-73.8]
[563,"Lévis","QC",5050,-25,28,10,14,7,12,8,-12,-9,-3,4,12,17,20,19,15,7,1,-6,46.8,-71.180000000000007]
[564,"Loretteville","QC",5200,-26,28,11,14,7,17,11,-14,-10,-3,3,12,17,20,19,13,7,-1,-9,46.85,-71.349999999999994]
[565,"Louiseville","QC",4900,-25,29,12,15,9,18,17,-13,-11,-4,4,12,17,20,19,13,7,0,-8,46.25,-72.95]
[566,"Magog","QC",4730,-26,29,10,15,8,9,8,-10,-9,-3,5,12,17,19,18,13,7,1,-7,45.27,-72.13]
[567,"Malartic","QC",6200,-33,29,12,12,6,13,11,-17,-15,-8,1,9,15,17,16,10,4,-4,-13,48.13,-78.13]
[568,"Maniwaki","QC",5280,-30,29,12,14,8,8,7,-12,-10,-3,4,12,17,19,18,14,7,0,-7,46.38,-75.97]
[569,"Masson","QC",4610,-26,30,12,15,9,11,9,-12,-11,-4,5,13,18,20,19,14,8,1,-8,45.533299999999997,-75.416700000000006]
[570,"Matane","QC",5510,-24,24,9,13,7,22,15,-12,-11,-6,1,8,14,17,16,11,6,-1,-7,48.85,-67.53]
[571,"Mont-Joli","QC",5370,-24,26,9,14,7,22,15,-12,-11,-5,2,9,15,18,17,12,6,0,-7,48.58,-68.180000000000007]
[572,"Mont-Laurier","QC",5320,-29,29,13,14,7,8,7,-14,-12,-5,3,11,16,18,17,12,6,-1,-10,46.55,-75.5]
[573,"Montmagny","QC",5090,-25,28,11,14,7,23,15,-12,-10,-4,3,11,16,19,18,13,6,0,-8,46.98,-70.55]
[574,"Montréal (city hall)","QC",4200,-23,30,8,15,9,12,11,-8,-6,-1,7,14,19,22,21,17,10,3,-4,45.508899999999997,-73.553600000000003]
[575,"Montréal-Est","QC",4470,-23,30,9,15,9,13,11,-9,-7,-2,6,14,19,21,21,16,9,2,-4,45.63,-73.52]
[576,"Montréal-Nord","QC",4470,-24,30,9,15,9,13,11,-11,-9,-3,5,13,17,20,19,14,7,1,-7,45.6,-73.63]
[577,"Nicolet (Gentilly)","QC",4900,-25,29,10,15,9,14,13,-11,-9,-3,5,13,18,20,19,15,8,2,-6,46.4,-72.28]
[578,"Nitchequon","QC",8100,-39,23,9,12,2,16,15,-24,-22,-15,-6,2,10,14,12,6,0,-8,-20,53.21,-70.91]
[579,"Noranda","QC",6050,-33,29,10,12,6,12,12,-16,-13,-6,2,10,16,18,17,13,5,-3,-10,48.25,-79.02]
[580,"Outremont","QC",4300,-23,30,9,15,9,13,11,-10,-7,-2,6,14,19,22,20,15,8,2,-6,45.52,-73.62]
[581,"Percé","QC",5400,-21,25,6,11,7,18,13,-9,-9,-4,1,6,12,16,16,12,6,1,-5,48.53,-64.22]
[582,"Pierrefonds","QC",4430,-24,30,9,15,9,17,12,-10,-9,-3,6,13,18,21,20,15,8,2,-7,45.48,-73.87]
[583,"Pincourt","QC",4480,-24,29,10,15,9,15,11,-10,-8,-2,6,13,19,21,20,16,9,2,-5,45.38,-73.98]
[584,"Plessisville","QC",5100,-26,29,12,15,8,13,11,-12,-11,-4,4,11,17,19,18,13,6,0,-8,46.22,-71.78]
[585,"Port-Cartier","QC",6060,-28,25,9,11,6,16,12,-15,-14,-7,0,6,12,15,15,10,4,-3,-10,50.02,-66.87]
[586,"Puvinrituq","QC",9200,-36,23,6,9,-1,18,22,-25,-26,-20,-10,-2,5,10,10,6,1,-7,-16,60.033299999999997,-77.283299900000003]
[587,"Québec","QC",5080,-25,28,10,14,7,12,8,-12,-9,-3,4,12,17,20,19,15,7,1,-6,46.8,-71.23]
[588,"Richmond","QC",4700,-25,29,12,14,7,11,7,-11,-9,-3,5,12,17,20,18,13,7,1,-7,45.67,-72.150000000000006]
[589,"Rimouski","QC",5300,-25,26,10,12,7,20,13,-12,-10,-4,3,10,15,18,17,12,6,0,-8,48.43,-68.55]
[590,"Rivière-du-Loup","QC",5380,-25,26,9,14,7,11,8,-12,-10,-5,2,9,15,17,17,12,6,0,-7,47.83,-69.53]
[591,"Roberval","QC",5750,-31,28,10,13,6,14,13,-16,-14,-7,2,10,16,18,17,12,6,-2,-11,48.52,-72.23]
[592,"Rock-Island","QC",4850,-25,29,11,15,8,10,8,-10,-9,-3,5,12,16,19,18,13,7,1,-7,45.04,-72.099999999999994]
[593,"Rosemère","QC",4550,-24,29,11,15,9,13,11,-10,-9,-3,6,13,18,21,20,15,8,2,-7,45.63,-73.8]
[594,"Rouyn","QC",6050,-33,29,10,12,6,12,12,-16,-13,-6,2,10,16,18,17,13,5,-3,-10,48.23,-79.02]
[595,"Saguenay","QC",5700,-30,28,11,14,6,16,11,-15,-14,-5,3,11,17,19,18,12,6,-1,-12,48.43,-71.069999999999993]
[596,"Saguenay (Bagotville)","QC",5700,-31,28,11,13,6,16,11,-16,-13,-6,2,10,16,18,17,12,5,-2,-10,48.35,-70.88]
[597,"Saguenay (Jonquière)","QC",5650,-30,28,11,14,6,15,12,-15,-13,-6,2,10,16,18,17,13,6,-1,-9,48.42,-71.22]
[598,"Saguenay (Kénogami)","QC",5650,-30,28,11,14,6,15,12,-15,-13,-6,2,10,16,18,17,13,6,-1,-9,48.42,-71.25]
[599,"Saint-Eustache","QC",4500,-25,29,9,15,9,17,12,-10,-9,-3,6,13,18,21,20,15,8,2,-7,45.56,-73.900000000000006]
[600,"Saint-Jean-sur-Richelieu","QC",4450,-24,29,11,15,9,14,10,-10,-8,-2,6,13,18,21,20,15,8,2,-6,45.31,-73.260000000000005]
[601,"Salaberry-de-Valleyfield","QC",4400,-23,29,10,15,9,14,10,-10,-8,-2,6,14,19,21,20,15,8,2,-6,45.25,-74.13]
[602,"Schefferville","QC",8550,-37,24,9,8,1,16,15,-24,-23,-16,-7,2,9,13,12,7,-1,-9,-18,54.8,-66.83]
[603,"Senneterre","QC",6180,-34,29,13,12,6,13,11,-19,-16,-9,1,9,14,17,15,10,4,-4,-14,48.38,-77.23]
[604,"Sept-Îles","QC",6200,-29,24,8,10,6,16,12,-15,-14,-7,0,6,12,15,15,10,4,-3,-10,50.2,-66.38]
[605,"Shawinigan","QC",5050,-26,29,11,15,8,10,9,-13,-11,-4,4,12,17,20,18,13,7,0,-9,46.55,-72.75]
[606,"Shawville","QC",4880,-27,30,13,15,9,12,9,-12,-10,-4,5,12,17,20,18,13,7,0,-8,45.6,-76.48]
[607,"Sherbrooke","QC",4700,-28,29,12,15,8,11,7,-11,-9,-4,4,11,16,18,18,13,7,1,-7,45.42,-71.900000000000006]
[608,"Sillery","QC",5070,-25,28,10,16,7,12,8,-12,-9,-3,4,12,17,20,19,15,7,1,-6,46.77,-71.25]
[609,"Sorel","QC",4550,-25,29,11,15,9,17,16,-11,-9,-3,5,13,18,21,20,14,8,1,-7,46.03,-73.12]
[610,"Ste-Agathe-des-Monts","QC",5390,-28,28,11,14,7,12,9,-13,-10,-5,3,11,15,18,16,12,6,-1,-10,46.05,-74.28]
[611,"Ste-Anne-de-Bellevue","QC",4460,-24,29,10,15,9,15,11,-10,-8,-2,6,13,19,21,20,16,9,2,-5,45.42,-73.930000000000007]
[612,"Ste-Foy","QC",5100,-25,28,10,16,7,12,8,-12,-9,-3,4,12,17,20,19,15,7,1,-6,46.78,-71.28]
[613,"St-Félicien","QC",5850,-32,28,12,14,6,15,12,-17,-15,-7,2,10,16,18,17,12,6,-3,-12,48.65,-72.45]
[614,"St-Georges-de-Cacouna","QC",5400,-25,26,9,14,7,11,8,-12,-10,-5,2,9,15,17,17,12,6,0,-7,47.92,-69.5]
[615,"St-Hubert","QC",4490,-24,30,11,15,9,18,13,-10,-8,-2,6,13,18,21,20,15,8,2,-6,45.5,-73.42]
[616,"St-Hubert-de-Rivière-du-Loup","QC",5520,-26,26,11,14,6,11,8,-15,-13,-6,1,9,15,17,16,11,5,-2,-11,47.816699999999997,-69.150000000000006]
[617,"St-Hyacinthe","QC",4500,-24,30,11,15,9,13,9,-11,-9,-3,6,13,19,21,20,15,8,1,-7,45.62,-72.95]
[618,"St-Jérôme","QC",4820,-26,29,11,15,9,13,8,-12,-10,-4,5,12,17,20,18,13,7,0,-8,45.78,-74]
[619,"St-Jovite","QC",5250,-29,28,14,14,7,5,5,-12,-11,-4,3,11,16,18,17,13,6,0,-8,46.12,-74.599999999999994]
[620,"St-Lambert","QC",4400,-23,30,11,15,9,18,13,-10,-8,-2,6,13,18,21,20,15,8,2,-6,45.5,-73.5]
[621,"St-Laurent","QC",4270,-23,30,10,15,9,17,12,-10,-8,-2,6,14,19,21,20,16,9,2,-5,45.5,-73.67]
[622,"St-Lazare-Hudson","QC",4520,-24,30,13,15,8,15,11,-13,-10,-3,5,12,17,20,18,13,7,0,-8,45.4,-74.14]
[623,"St-Nicolas","QC",4990,-25,28,10,14,7,14,9,-12,-9,-3,4,12,17,20,19,15,7,1,-6,46.7,-71.400000000000006]
[624,"Sutton","QC",4600,-25,29,11,15,8,10,7,-9,-8,-2,6,12,17,20,18,14,8,1,-6,45.1,-72.62]
[625,"Tadoussac","QC",5450,-26,27,10,13,7,26,14,-13,-11,-5,2,9,14,17,16,11,5,-1,-9,48.15,-69.72]
[626,"Témiscaming","QC",5020,-30,30,11,13,8,10,8,-11,-8,-3,4,11,17,19,19,15,7,1,-6,46.72,-79.099999999999994]
[627,"Terrebonne","QC",4500,-25,29,11,15,8,13,11,-12,-9,-3,5,13,18,21,20,14,7,1,-7,45.69,-73.63]
[628,"Thetford Mines","QC",5120,-26,28,10,14,7,13,10,-12,-11,-5,3,11,16,18,17,12,6,-1,-8,46.08,-71.3]
[629,"Thurso","QC",4820,-26,30,12,15,9,11,9,-13,-9,-3,5,13,18,21,19,14,8,1,-8,45.6,-75.25]
[630,"Trois-Rivières","QC",4900,-25,29,8,15,9,14,13,-10,-8,-3,4,12,18,21,20,15,9,2,-5,46.35,-72.55]
[631,"Val-d'Or","QC",6180,-33,29,11,12,6,13,11,-17,-14,-8,1,10,15,18,16,11,5,-3,-12,48.1,-77.78]
[632,"Varennes","QC",4500,-24,30,11,15,9,17,11,-10,-8,-2,6,13,19,20,19,15,8,2,-5,45.68,-73.430000000000007]
[633,"Verchères","QC",4450,-24,30,11,15,9,17,11,-10,-9,-3,6,13,18,21,20,15,8,1,-6,45.78,-73.349999999999994]
[634,"Verdun","QC",4200,-23,30,10,15,9,17,12,-10,-8,-2,6,14,19,21,20,16,9,2,-5,45.45,-73.569999999999993]
[635,"Victoriaville","QC",4900,-26,29,11,15,8,12,10,-12,-9,-3,5,13,17,20,19,13,7,1,-8,46.05,-71.97]
[636,"Ville-Marie","QC",5550,-31,30,11,13,7,11,10,-15,-12,-6,2,11,17,20,18,13,7,-1,-10,47.33,-79.430000000000007]
[637,"Wakefield","QC",4820,-27,30,13,15,8,11,9,-12,-10,-3,5,13,17,20,18,13,7,0,-8,45.64,-75.930000000000007]
[638,"Waterloo","QC",4650,-25,29,12,15,9,10,7,-11,-10,-3,5,12,16,19,18,13,7,1,-7,45.35,-72.52]
[639,"Windsor","QC",4700,-25,29,11,15,8,11,7,-11,-9,-4,4,11,16,18,18,13,7,1,-7,45.57,-72]
[640,"Assiniboia","SK",5180,-32,31,13,12,7,18,14,-12,-9,-4,5,11,16,19,19,13,5,-3,-9,49.63,-105.98]
[641,"Battrum","SK",5080,-32,32,14,10,6,20,15,-13,-10,-3,5,12,16,19,18,12,6,-4,-10,50.55,-108.33]
[642,"Biggar","SK",5720,-34,30,13,11,6,12,13,-16,-13,-5,4,11,16,18,17,11,5,-6,-14,52.07,-108]
[643,"Broadview","SK",5760,-34,30,12,12,6,17,14,-15,-12,-6,4,11,16,18,17,11,4,-6,-12,50.37,-102.58]
[644,"Dafoe","SK",5860,-35,29,12,12,5,14,12,-17,-13,-6,3,11,16,18,17,11,4,-6,-14,51.75,-104.53]
[645,"Dundurn","SK",5600,-35,30,12,12,6,14,13,-16,-12,-5,-5,11,16,18,17,11,4,-6,-14,51.82,-106.5]
[646,"Estevan","SK",5340,-32,32,13,13,6,18,14,-14,-10,-4,5,12,17,19,19,12,5,-5,-11,49.13,-102.98]
[647,"Hudson Bay","SK",6280,-36,29,13,12,5,11,11,-18,-14,-7,2,9,14,18,16,11,3,-7,-15,52.85,-102.38]
[648,"Humboldt","SK",6000,-36,28,13,13,5,14,13,-17,-14,-7,3,11,15,17,16,11,4,-7,-15,52.2,-105.12]
[649,"Island Falls","SK",7100,-39,27,12,12,4,10,13,-23,-19,-11,0,8,14,17,16,9,2,-9,-20,55.53,-102.35]
[650,"Kamsack","SK",6040,-34,29,14,14,5,13,11,-19,-15,-8,3,11,16,18,17,11,4,-7,-16,51.57,-101.9]
[651,"Kindersley","SK",5550,-33,31,13,10,6,14,14,-14,-11,-4,5,11,15,18,17,12,4,-6,-11,51.47,-109.17]
[652,"Lloydminster","SK",5880,-34,28,12,11,5,15,14,-14,-11,-6,4,10,15,17,16,10,3,-7,-12,53.28,-110]
[653,"Maple Creek","SK",4780,-31,31,14,10,7,13,13,-9,-6,-2,6,10,15,19,18,13,6,-2,-6,49.92,-109.48]
[654,"Meadow Lake","SK",6280,-38,28,12,11,4,11,11,-17,-14,-7,4,10,15,17,16,10,3,-8,-15,54.13,-108.43]
[655,"Melfort","SK",6050,-36,28,12,13,5,15,13,-17,-13,-8,3,10,15,18,17,11,3,-6,-13,52.87,-104.62]
[656,"Melville","SK",5880,-34,29,13,12,5,15,13,-20,-15,-8,3,11,16,18,16,11,5,-6,-15,50.92,-102.8]
[657,"Moose Jaw","SK",5270,-32,31,14,12,7,18,15,-12,-9,-4,6,11,15,19,18,13,5,-3,-8,50.4,-105.53]
[658,"Nipawin","SK",6300,-37,28,12,13,5,13,12,-18,-15,-7,3,11,16,18,16,10,3,-9,-17,53.37,-104]
[659,"North Battleford","SK",5900,-34,29,12,11,5,12,13,-16,-12,-6,4,11,15,18,17,11,4,-7,-14,52.78,-108.28]
[660,"Prince Albert","SK",6100,-37,28,12,13,5,10,12,-17,-14,-7,3,10,15,18,17,11,3,-7,-15,53.2,-105.77]
[661,"Qu'Appelle","SK",5620,-34,30,13,13,6,18,14,-15,-12,-5,4,11,16,18,18,12,5,-6,-13,50.55,-103.88]
[662,"Regina","SK",5600,-34,31,13,12,6,19,16,-15,-12,-5,5,11,16,19,18,12,4,-5,-12,50.45,-104.62]
[663,"Rosetown","SK",5620,-34,31,14,10,6,15,14,-16,-12,-6,4,10,15,18,17,12,4,-5,-11,51.55,-108]
[664,"Saskatoon","SK",5700,-35,30,13,12,6,15,14,-16,-12,-6,5,11,16,18,17,11,4,-6,-13,52.12,-106.63]
[665,"Scott","SK",5960,-34,30,13,11,5,12,13,-15,-11,-7,4,10,14,18,17,11,3,-5,-11,52.37,-108.83]
[666,"Strasbourg","SK",5600,-34,30,13,13,6,14,12,-17,-12,-5,4,12,17,19,18,11,5,-5,-13,51.07,-104.95]
[667,"Swift Current","SK",5150,-31,31,12,10,6,22,17,-11,-8,-3,5,11,15,18,18,12,5,-3,-8,50.28,-107.8]
[668,"Uranium City","SK",7500,-42,26,10,11,3,8,11,-24,-19,-13,-3,5,13,16,14,8,0,-11,-18,59.57,-108.62]
[669,"Weyburn","SK",5400,-33,31,13,14,6,18,15,-15,-11,-6,5,11,16,19,19,13,5,-4,-11,49.67,-103.85]
[670,"Yorkton","SK",6000,-34,29,12,12,5,14,12,-17,-13,-7,3,10,15,18,17,11,4,-7,-14,51.22,-102.47]
[671,"Aishihik","YT",7500,-44,23,13,7,2,4,8,-23,-18,-10,0,8,13,15,13,7,-2,-15,-21,61.6,-137.51669999999999]
[672,"Dawson","YT",8120,-50,26,13,7,1,1,4,-27,-22,-12,0,8,14,16,13,6,-5,-18,-25,64.069999999999993,-139.41999999999999]
[673,"Destruction Bay","YT",7800,-43,23,13,6,2,9,13,-19,-16,-12,-3,5,11,13,10,5,-3,-15,-17,61.25,-138.80000000000001]
[674,"Faro","YT",7300,-46,25,11,8,2,6,6,-23,-15,-9,1,7,14,15,12,7,-2,-15,-18,62.226999999999997,-133.357]
[675,"Haines Junction","YT",7100,-45,24,13,6,3,4,8,-20,-12,-7,1,7,12,13,12,7,0,-13,-16,60.78,-137.54]
[676,"Snag","YT",8300,-51,23,13,9,2,3,6,-27,-21,-13,-2,6,12,14,11,5,-7,-20,-25,62.4,-140.37]
[677,"Teslin","YT",6770,-42,24,12,7,4,4,7,-19,-13,-8,0,6,12,14,12,7,1,-10,-14,60.17,-132.72]
[678,"Watson Lake","YT",7470,-46,26,11,7,4,3,9,-23,-18,-10,0,8,13,15,13,7,-1,-15,-20,60.13,-128.71]
[679,"Whitehorse","YT",6580,-41,25,11,7,3,13,10,-17,-12,-7,1,7,12,14,12,7,0,-10,-12,60.72,-135.05000000000001]
[680,"TestSite","Test",100,101,102,103,104,105,106,107,108,109,110,111,112,113,114,115,116,117,118,119,120,121]

{"sheet":"Wall_R_value","index":6,"n_rows":13,"n_cols":4,"rows_kept":13,"cut":false,"hidden":false,"merged":[]}
["No.","Wall Type","R value","RSI"]
[1,"Wall Type 1",5,{"$f":"C2*0.176","v":0.87999999999999989}]
[2,"Wall Type 2",10,{"$f":"C3*0.176","v":1.7599999999999998}]
[3,"Wall Type 3",15,2.6399999999999997]
[4,"Wall Type 4",20,3.5199999999999996]
[5,"Wall Type 5",25,4.3999999999999995]
[6,"Wall Type 6",30,5.2799999999999994]
[7,"Wall Type 7",35,6.1599999999999993]
[8,"Wall Type 8",40,7.0399999999999991]
[9,"Wall Type 9",45,7.92]
[10,"Wall Type 10",50,8.7999999999999989]
[11,"Wall Type 11",55,9.68]
[12,"Wall Type 12",60,10.559999999999999]

{"sheet":"WindowData","index":7,"n_rows":22,"n_cols":5,"rows_kept":22,"cut":false,"hidden":false,"merged":[]}
["No.","Window Type","R value","RSI","Solar heat gain co."]
[null,null,"w/m2.degC","btu/sqft.F","SHGC"]
[1,"Window Type 1",{"$f":"D3*0.175","v":0.17499999999999999},1,0.65]
[2,"Window Type 2",{"$f":"D4*0.175","v":0.35},2,0.65]
[3,"Window Type 3",0.52499999999999991,3,0.65]
[4,"Window Type 4",0.7,4,0.65]
[5,"Window Type 5",0.875,5,0.65]
[6,"Window Type 6",1.0499999999999998,6,0.65]
[7,"Window Type 7",1.2249999999999999,7,0.65]
[8,"Window Type 8",1.4,8,0.65]
[9,"Window Type 9",1.575,9,0.65]
[10,"Window Type 10",1.75,10,0.65]
[11,"Window Type 1",{"$f":"D13*0.175","v":0.17499999999999999},1,0.4]
[12,"Window Type 2",0.35,2,0.4]
[13,"Window Type 3",0.52499999999999991,3,0.4]
[14,"Window Type 4",0.7,4,0.4]
[15,"Window Type 5",0.875,5,0.4]
[16,"Window Type 6",1.0499999999999998,6,0.4]
[17,"Window Type 7",1.2249999999999999,7,0.4]
[18,"Window Type 8",1.4,8,0.4]
[19,"Window Type 9",1.575,9,0.4]
[20,"Window Type 10",1.75,10,0.4]

{"sheet":"RoofData","index":8,"n_rows":13,"n_cols":4,"rows_kept":13,"cut":false,"hidden":false,"merged":[]}
["No.","Wall Type","R value","RSI"]
[1,"Roof Type 1",5,{"$f":"C2*0.176","v":0.87999999999999989}]
[2,"Roof Type 2",10,{"$f":"C3*0.176","v":1.7599999999999998}]
[3,"Roof Type 3",15,2.6399999999999997]
[4,"Roof Type 4",20,3.5199999999999996]
[5,"Roof Type 5",25,4.3999999999999995]
[6,"Roof Type 6",30,5.2799999999999994]
[7,"Roof Type 7",35,6.1599999999999993]
[8,"Roof Type 8",40,7.0399999999999991]
[9,"Roof Type 9",45,7.92]
[10,"Roof Type 10",50,8.7999999999999989]
[11,"Roof Type 11",55,9.68]
[12,"Roof Type 12",60,10.559999999999999]