## hood size by area of hood
KITCHEN HOOD CAPACITY CALCULATION
METHOD 1: PROTECTION AREA OF THE HOOD
L(FT) | W(FT) | AIR FLOW PER AREA OF HOOD (CFM/SQFT) |  | AIRFLOW(CFM) |  |  | E/A AIR FLOW (CFM)
6 | 2.5 | 80 |  | 6x2.5x80 |  |  | 1200
KITCHEN HOOD CAPACITY CALCULATION
METHOD 1: VERTICAL AREA OF THE HOOD
L(FT) | W1(FT) | W2(FT) | H(FT) | AIR FLOW PER VERTICAL AREA (CFM/SQFT) |  | AIRFLOW(CFM) | E/A AIR FLOW (CFM)
6 | 2.5 | 2.5 | 3.5 | 50 |  | (6+2.5+2.5)x3.5x50 | 1925 | 1732.5
METHOD 2: APPLIANCE TYPE
ELEC COOK(FT) | GAS COOK(FT) | APPLIANCE | ELECTRICAL COOKING APPLIANCE (CFM/LINEAR FT) | GAS COOKING APPLIANCE (CFM/LINEAR FT) | AIRFLOW(CFM) |  | E/A AIR FLOW (CFM)
3 | 0 | BREAD OVEN | 155 | 175 | 3x375+0x435 |  | 465
1.75 | 0 | RAPID COOK OVEN | 180 | 205 | 1.75x375+0x450 |  | 315
TOTAL E/A AIR FLOW (CFM) | [6 empty] | 780
THE EXHAUST HOOD AIR FLOW IS SPECIFED TO BE 1925 CFM.