## Metric Water
Pump Selection Worksheet
| Project: |  |  | Bonnyville and District Centennial Centre |  |  | Date Created: | 2005-03-14
| Project No.: |  |  | 3791-99 |  |  | Date Printed: | 2021-02-15 19:58
| File Name: |  |  | C:\Users\Administrator\Documents\
| Created by: |  |  | MJR
Section 1 - Design Flow Rate (Secondary Heating Pumps P-xx/xx)
|  |  | Total Load (kW) | 1560 |  | Heating Media | 82.2oC Water
|  |  | Heating Water Flow (l/s) | 26.7215 |  | Specific Heat (J/kgoC) | 4.2
|  |  | Design Flow (l/s) | 16.0329 |  | DT (oC) | 13.9
[6 empty] | Design Flow | 60%
[6 empty] | Design Friction (ft/100ft) | 2
Section 2 - Head Loss
|  | Equipment |  | # or Length | Equivalent Length/Equipment | Equivalent Length
|  | Pipe Length (ft) |  | 950 | 1 | 950
|  | Pipe Fittings (50% of Pipe Length) |  | 475 | 1 | 475
|  | Globe Valve |  | 1 | 168 | 168
|  | Gate Valve |  | 2 | 3.54 | 7.08
|  | Strainer |  | 1 | 84.1 | 84.1
|  | Check Valve |  | 1 | 42.1 | 42.1
|  | Balancing Valve |  |  |  | 0
|  | Terminal Run (Rad. Panel Lab 1175) |  | 1 | 183 | 183
|  |  | Gate Valve | 2 | 0.61 | 1.22
|  |  | Control Valve | 1 | 0.61 | 0.61
|  |  | Balancing Valve | 1 | 29.1 | 29.1
|  |  | Elbows (90o) | 11 | 2.6 | 28.6
|  | Total Equivalent Length (ft) |  |  |  | 1940.21
Section 3 - Total Friction Loss
|  | Piping Losses (ft) |  | 38.8042
HEX Losses (ft)
Boiler Losses (ft)
Terminal Unit Losses (ft)
|  | Total Losses (ft) w/ 10% S.F. |  | 42.6846
|  | Total Losses (kPa) |  | 127.627

## Imperial Water
Pump Selection Worksheet
| Project: | [5 empty] | Date Created: | 2005-07-07
| Project No.: | [5 empty] | Date Printed: | 2021-02-15 19:58
| File Name: |  |  | C:\Users\Administrator\Documents\
Created by:
Section 1 - Design Flow Rate (Building Heating Pumps P-xx/xx)
|  |  | Total Load (BTU/hr) | 2800000 |  | Heating Media | 180oF Water
|  |  | Heating Media Flow (GPM) | 280 |  | Specific Heat | 500
|  |  | Design Flow (GPM) | 280 |  | DT (oF) | 20
[6 empty] | Design Flow | 100%
[6 empty] | Design Friction (ft/100ft) | 2.5
Section 2 - Head Loss
|  | Equipment |  | # or Length | Equivalent Length/Equipment | Equivalent Length
|  | Pipe Length (ft) |  | 750 | 1 | 750
|  | Pipe Fittings (50% of Pipe Length) |  | 375 | 1 | 375
|  | Globe Valve |  | 1 | 112 | 112
|  | Gate Valve |  | 2 | 2.35 | 4.7
|  | Strainer |  | 1 | 56 | 56
|  | Check Valve |  | 1 | 28 | 28
|  | Balancing Valve |  | 2 | 112 | 224
|  | Terminal Run (IHP-1) |  |  |  | 0
|  |  | Gate Valve |  |  | 0
|  |  | Control Valve |  |  | 0
|  |  | Balancing Valve |  |  | 0
|  |  | Elbows (90o) |  |  | 0
|  | Total Equivalent Length (ft) |  |  |  | 1549.7
Section 3 - Total Friction Loss
|  | Piping Losses (ft) |  | 38.7425
|  | HEX Losses (ft) |  | 16
|  | Boiler Losses (ft) |  | 9
Terminal Unit Losses (ft)
|  | Total Losses (ft) w/ 10% S.F. |  | 70.1168
|  | Total Losses (kPa) |  | 209.6491

## Sheet1
0.87
|  | Pipe Size | Pipe Length | Ft | Fitting (50%) | Flow | Loss (ft/100) | Loss (ft) | Supply | Pipe Size | Pipe Length | ft | Fitting (50%) | Flow | Loss (ft/100) | Loss (ft) | Return |  | Terminal
282 |  | 4 | 16 | 52.4928 | 78.7392 | 282 | 4.3 | 3.3858 | 3.3858 | 0.75 | 6 | 19.6848 | 29.5272 | 1.2 | 1 | 0.29527 | 41.3479 | 44.7337
| 78 | 4 | 15 | 49.212 | 73.818 | 214.14 | 2.7 | 1.9931 | 5.3789 | 1 | 12 | 39.3696 | 59.0544 | 3.0711 | 1 | 0.59054 | 41.0527 | 46.4315
| 1.33 | 4 | 6 | 19.6848 | 29.5272 | 212.9829 | 2.7 | 0.79723 | 6.1761 | 1 | 5 | 16.404 | 24.606 | 4.2891 | 1.3 | 0.31988 | 40.4621 | 46.6382
| 2.2 | 4 | 12 | 39.3696 | 59.0544 | 211.0689 | 2.7 | 1.5945 | 7.7706 | 1 | 5.2 | 17.0602 | 25.5902 | 4.9851 | 2 | 0.5118 | 40.1422 | 47.9128
| 1.4 | 4 | 5 | 16.404 | 24.606 | 209.8509 | 2.5 | 0.61515 | 8.3857 | 1.25 | 5 | 16.404 | 24.606 | 18.3831 | 6 | 1.4764 | 39.6304 | 48.0161
| 0.8 | 4 | 5.2 | 17.0602 | 25.5902 | 209.1549 | 2.5 | 0.63976 | 9.0255 | 1.25 | 5 | 16.404 | 24.606 | 19.3401 | 6 | 1.4764 | 38.1541 | 47.1795
| 15.4 | 4 | 5 | 16.404 | 24.606 | 195.7569 | 2.2 | 0.54133 | 9.5668 | 1.25 | 12 | 39.3696 | 59.0544 | 21.0801 | 6 | 3.5433 | 36.6777 | 46.2445
| 1.1 | 4 | 5 | 16.404 | 24.606 | 194.7999 | 2.2 | 0.54133 | 10.1081 | 1.5 | 3 | 9.8424 | 14.7636 | 21.6891 | 6 | 0.88582 | 33.1344 | 43.2426
| 2 | 4 | 12 | 39.3696 | 59.0544 | 193.0599 | 2 | 1.1811 | 11.2892 | 2 | 6.5 | 21.3252 | 31.9878 | 22.8201 | 1.2 | 0.38385 | 32.2486 | 43.5379
| 0.7 | 4 | 3 | 9.8424 | 14.7636 | 192.4509 | 2 | 0.29527 | 11.5845 | 2 | 6.5 | 21.3252 | 31.9878 | 23.8641 | 1.4 | 0.44783 | 31.8648 | 43.4493
| 1.3 | 4 | 6.5 | 21.3252 | 31.9878 | 191.3199 | 2 | 0.63976 | 12.2243 | 2 | 5 | 16.404 | 24.606 | 32.0421 | 2.2 | 0.54133 | 31.4169 | 43.6412
| 1.2 | 4 | 6.5 | 21.3252 | 31.9878 | 190.2759 | 2 | 0.63976 | 12.864 | 2 | 13.5 | 44.2908 | 66.4362 | 34.4781 | 2.6 | 1.7273 | 30.8756 | 43.7396
| 9.4 | 4 | 5 | 16.404 | 24.606 | 182.0979 | 1.9 | 0.46751 | 13.3315 | 2.5 | 10 | 32.808 | 49.212 | 44.0481 | 1.7 | 0.8366 | 29.1483 | 42.4798
| 2.8 | 4 | 13.5 | 44.2908 | 66.4362 | 179.6619 | 1.9 | 1.2623 | 14.5938 | 2.5 | 15 | 49.212 | 73.818 | 53.6181 | 2.3 | 1.6978 | 28.3117 | 42.9055
| 11 | 4 | 10 | 32.808 | 49.212 | 170.0919 | 1.7 | 0.8366 | 15.4304 | 2.5 | 18 | 59.0544 | 88.5816 | 63.1881 | 3 | 2.6574 | 26.6138 | 42.0443
| 11 | 4 | 15 | 49.212 | 73.818 | 160.5219 | 17 | 12.5491 | 27.9795 | 2.5 | 18 | 59.0544 | 88.5816 | 72.7581 | 4 | 3.5433 | 23.9564 | 51.9359
| 11 | 4 | 18 | 59.0544 | 88.5816 | 150.9519 | 1.4 | 1.2401 | 29.2196 | 2.5 | 18 | 59.0544 | 88.5816 | 82.3281 | 5 | 4.4291 | 20.4131 | 49.6328
| 11 | 4 | 18 | 59.0544 | 88.5816 | 141.3819 | 1.4 | 1.2401 | 30.4598 | 2.5 | 16 | 52.4928 | 78.7392 | 91.8981 | 6 | 4.7244 | 15.9841 | 46.4438
| 11 | 4 | 18 | 59.0544 | 88.5816 | 131.8119 | 1 | 0.88582 | 31.3456 | 2.5 | 10 | 32.808 | 49.212 | 93.4641 | 6.5 | 3.1988 | 11.2597 | 42.6053
| 11 | 4 | 16 | 52.4928 | 78.7392 | 122.2419 | 1 | 0.78739 | 32.133 | 4 | 7 | 22.9656 | 34.4484 | 210.0441 | 2.5 | 0.86121 | 8.0609 | 40.1939
| 1.8 | 4 | 10 | 32.808 | 49.212 | 120.6759 | 1 | 0.49212 | 32.6251 | 4 | 5 | 16.404 | 24.606 | 211.0011 | 2.5 | 0.61515 | 7.1997 | 39.8248
| 134 | 1 | 7 | 22.9656 | 34.4484 | 4.0959 | 1.2 | 0.41338 | 33.0385 | 4 | 11 | 36.0888 | 54.1332 | 212.7411 | 2.5 | 1.3533 | 6.5846 | 39.623
| 1.1 | 1 | 5 | 16.404 | 24.606 | 3.1389 | 1 | 0.24606 | 33.2845 | 4 | 15 | 49.212 | 73.818 | 214.1 | 2.5 | 1.8455 | 5.2312 | 38.5158
| 2 | 0.75 | 11 | 36.0888 | 54.1332 | 1.3989 | 1 | 0.54133 | 33.8259 | 4 | 16 | 52.4928 | 78.7392 | 290.7411 | 4.3 | 3.3858 | 3.3858 | 37.2117
| 2 |  | 243.7 | 799.531 | 1199.2964 | [5 empty] | 243.7 | 799.531 | 1199.2964
[17 empty] | Max Loss | 51.9359