## FP HYDRAULIC CALC
FIRE SPRINKLER (NFPA13) HYDRAULIC CALCULATIONS
SPREADSHEET DEVELOPPED BY TAN, XIANGYANG P.ENG
HAZE WILLIAMS METHOD
COMPANY | XT ENGINEERING LTD.
DESIGNER | X.Tan
CLIENT | AGELESS BEAUTY LASER AND SPA
PROJECT | UNIT 111 | 8645 160TH SURREY BC
JOB NO | X19005C | DATE | 2019-01-31
HAZARD CLASSIFICATION |  |  | OH1
DENSITY |  |  | 0.15 | GPM/SQFT
MAXIMUM COVERAGE AREA |  |  | 472.5 | SQFT
WATER DEMAND |  |  | 70.875
DISCHARGING SPRINKLER |  |  | 5
MAXIMUM SPACING |  |  | 15 | FT
SINGLE SPRINKLER REQUIRED FLOW |  |  | 14.175 | GPM
ADDITION FLOW ALLOWANCE |  |  | 2.5 | GPM
PIPE | NODE | ELEV1 | K FACTOR | FLOW @ NODE | FLOW @ PIPE | PIPE SIZE |  | PIPE |  | TOTAL | FRICTION LOSS Pf | HEAD LOSS OVER PIPE Pf | ELEV PRESSURE Pe | RESIDUAL PRESSURE | PRESSURE AT NEXT NODE | ROUGHNESS COEFF. | WATER VELOCITY |  | VELOCITY PRESSURE | NOTES
| TO | ELEV2 |  |  |  | NOM. | ACTUAL | PIPE & | LENGTH | PIPE LENGTH | PER FT |  |  | Pt
NO. | NODE | FT |  | GPM | GPM | IN | IN. | FITTING | FT | FT | PSI | PSI | PSI | PSI | PSI |  | FT/SEC | M/S | PSI | ***
1 | 1 | 36 | 5.6 | 14.175 | 16.675 | 1 | 1.049 | STEEL | 2.8 | 10 | 0.09296 | 0.9296 | 0 | 6.4072 | 7.3368 | 120 | 5.238 | 1.5873 | 0.18482
| TO | [6 empty] | 1SE | 3.5
| 2 | 36 | [5 empty] | 1TT | 4
2 | 2 | 36 | 5.6 | 15.1685 | 31.8435 | 1.5 | 1.61 | STEEL | 2.2 | 10 | 0.038194 | 0.38194 | 0 | 7.3368 | 7.7188 | 120 | 4.9953 | 1.5137 | 0.16809
| TO | [6 empty] | 1SE | 3.5
| 3 | 36 | [5 empty] | 1TT | 4
3 | 3 | 36 | 5.6 | 15.5583 | 47.4018 | 1.5 | 1.61 | STEEL | 1.9 | 10 | 0.079732 | 0.79732 | 0 | 7.7188 | 8.5161 | 120 | 7.4359 | 2.2533 | 0.37246
| TO | [6 empty] | 1SE | 3.5
| 4 | 36 | [5 empty] | 1TT | 4
4 | 4A | 36 | 5.6 | 14.175 | 16.675 | 1 | 1.049 | STEEL | 2.8 | 10 | 0.09296 | 0.9296 | 0 | 6.4072 | 7.3368 | 120 | 5.238 | 1.5873 | 0.18482
| TO | [6 empty] | 1SE | 3.5
| 4 | 36 | [5 empty] | 1TT | 4
5 | 5A | 36 | 5.6 | 15.1685 | 17.6685 | 1.5 | 1.61 | STEEL | 2.8 | 10 | 0.012845 | 0.12845 | 0 | 7.3368 | 7.4653 | 120 | 2.3795 | 0.72106 | 0.03814
| TO | [6 empty] | 1SE | 3.5
| 5 | 36 | [5 empty] | 1TT | 4
pipe section below
3 | 4 | 36 |  |  | 65.0703 | 1.5 | 1.61 | STEEL | 32 | 35.5 | 0.14327 | 5.0862 | 0 | 7.7188 | 12.805 | 120 | 10.2076 | 3.0932 | 0.70187
| TO | [6 empty] | 1SE | 3.5
| 5 | 36 | [5 empty] | 1TT
4 | 5 | 75.4 |  |  | 65.0703 | 1.25 | 1.38 | CPVC | 1 | 4.5 | 0.30353 | 1.3659 | 3.5947 | 12.805 | 17.7656 | 120 | 13.8937 | 4.2102 | 1.3003
| TO | [6 empty] | 1SE | 3.5
| 6 | 67.1 | [5 empty] | 1TT
5 | 6 | 67.1 |  |  | 65.0703 | 1.25 | 1.38 | CPVC | 3.8 | 7.3 | 0.30353 | 2.2158 | 0 | 17.7656 | 19.9814 | 120 | 13.8937 | 4.2102 | 1.3003
| TO | [6 empty] | 1SE | 3.5
| 7 | 67.1 | [5 empty] | 1TT
6 | 7 | 67.1 |  |  | 65.0703 | 1.25 | 1.38 | CPVC | 13.8 | 21.3 | 0.30353 | 6.4652 | 0 | 19.9814 | 26.4466 | 120 | 13.8937 | 4.2102 | 1.3003
| TO | [6 empty] | 1SE | 3.5
| 8 | 67.1 | [5 empty] | 1TT | 4
7 | 8 | 67.1 |  |  | 65.0703 | 1.25 | 1.38 | CPVC | 10 | 17.5 | 0.26175 | 4.5807 | 4.331 | 26.4466 | 35.3582 | 130 | 13.8937 | 4.2102 | 1.3003
| TO | [6 empty] | 1SE | 3.5
| 9 | 57.1 | [5 empty] | 1TT | 4
8 | 8 | 67.1 |  |  | 65.0703 | 1.5 | 1.61 | CPVC | 10 | 13.5 | 0.12355 | 1.668 | 4.331 | 35.3582 | 41.3572 | 130 | 10.2076 | 3.0932 | 0.70187
| TO | [6 empty] | 1SE | 3.5
| 9 | 57.1 | [5 empty] | 1TT | 0
9 | 9 | 57.1 |  |  | 65.0703 | 1.5 | 1.61 | CPVC | 25 | 36.5 | 0.12355 | 4.5097 | 4.331 | 41.3572 | 50.1979 | 130 | 10.2076 | 3.0932 | 0.70187
| TO | [6 empty] | 1SE | 3.5
| 10 | 47.1 | [5 empty] | 1TT | 8
10 | HOSE | 47.1 |  | 0 | 65.0703 | 1.5 | 1.61 | STEEL | 10 | 10 | 0.12355 | 1.2355 | 1.7324 | 50.1979 | 53.1659 | 130 | 10.2076 | 3.0932 | 0.70187
| TO | [6 empty] | 1SE
| TEST | 43.1 | [5 empty] | 1TT
TEST |  | TEST | WATER FLOW= |  | 65.0703 | GPM | 4.1314 | L/S |  |  | REQUIRED PRESSURE= |  |  | 53.1659 | PSI | 366.313 | kPa | 36.6313 | mH2O
[11 empty] | SYSTEM K FACTOR = |  |  | 8.9241
Note on A36: Administrator: ABOVE BLUE LINE ARE DISCHARGE SPRINKLER NODES, BELOW ARE PIPING SECTIONS, YOU CAN ADD MORE NODES
Note on T36: Administrator: ABOVE BLUE LINE ARE DISCHARGE SPRINKLER NODES, BELOW ARE PIPING SECTIONS, YOU CAN ADD MORE NODES

## PIPE CHART
ASTM A53 PIPE SIZE (IN)
PIPE SIZE | 0.75 | 1 | 1.25 | 1.5 | 2 | 3 | 4 | 5 | 6 | 8
ACTUAL PIPE SIZE | 0.82 | 1.049 | 1.38 | 1.61 | 2.07 | 3.26 | 4.26 | 5.05 | 6.07 | 7.98

## PROJECT INFO
FIRE SPRINKLER (NFPA13, 13R) HYDRAULIC CALCULATIONS
SPREADSHEET DEVELOPPED BY TAN, XIANGYANG P.ENG
HAZE WILLIAMS METHOD
COMPANY | XT ENGINEERING LTD.
DESIGNER | X.Tan
CLIENT
PROJECT | FORSMAN GARDEN TOWNHOMES
JOB NO | X1724
HAZARD CLASSIFICATION |  | Light Hazard
DENSITY |  | 0.1 | GPM
MAXIMUM COVERAGE ARAE |  | 1500 | SQFT
DISCHARGING SPRINKLER |  | 8
MAXIMUM SPACING |  | 15 | FT
SINGLE SPRINKLER REQUIRED FLOW |  | 22.5 | GPM
ADDITION FLOW ALLOWANCE |  | 0 | GPM
Pipe Material | C factor of Hzaen Williams Equation
CPVC | 150
Steel | 130

## MATERIAL C
Material | Hazen-Williams Coefficient
- c -
ABS - Acrylonite Butadiene Styrene | 130
Aluminum | 130 - 150
Asbestos Cement | 140
Asphalt Lining | 130 - 140
Brass | 130 - 140
Brick sewer | 90 - 100
Cast-Iron - new unlined (CIP) | 130
Cast-Iron 10 years old | 107 - 113
Cast-Iron 20 years old | 89 - 100
Cast-Iron 30 years old | 75 - 90
Cast-Iron 40 years old | 64-83
Cast-Iron, asphalt coated | 100
Cast-Iron, cement lined | 140
Cast-Iron, bituminous lined | 140
Cast-Iron, sea-coated | 120
Cast-Iron, wrought plain | 100
Cement lining | 130 - 140
Concrete | 100 - 140
Concrete lined, steel forms | 140
Concrete lined, wooden forms | 120
Concrete, old | 100 - 110
Copper | 130 - 140
Corrugated Metal | 60
Ductile Iron Pipe (DIP) | 140
Ductile Iron, cement lined | 120
Fiber | 140
Fiber Glass Pipe - FRP | 150
Galvanized iron | 120
Glass | 130
Lead | 130 - 140
Metal Pipes - Very to extremely smooth | 130 - 140
Plastic | 130 - 150
Polyethylene, PE, PEH | 140
Polyvinyl chloride, PVC, CPVC | 150
Smooth Pipes | 140
Steel new unlined | 140 - 150
Steel, corrugated | 60
Steel, welded and seamless | 100
Steel, interior riveted, no projecting rivets | 110
Steel, projecting girth and horizontal rivets | 100
Steel, vitrified, spiral-riveted | 90 - 110
Steel, welded and seamless | 100
Tin | 130
Vitrified Clay | 110
Wrought iron, plain | 100
Wooden or Masonry Pipe - Smooth | 120
Wood Stave | 110 - 120