## Sheet1
Page 1 of 2
Water Meter Sizing Calculation Sheet
For Non-Fire Service Meters
Methodology: AWWA M22
General Information
Project Name: |  | Steveston Townhouse |  |  |  | PID Number:
Address: | 9571,9591,9611,9671 Steveston Hwy |  |  |  |  | Project Number: | [6 empty] | x20085
| Richmond, BC |  |  |  |  | Building Permit Number
Type of Occupancy: |  |  | Multi-Family |  |  |  |  | Institutional |  |  |  | Industrial
|  |  | Commercial |  |  |  |  | Other | [6 empty] | # of Units | 20
Is this a phased development? | [7 empty] | Yes |  |  |  | No
Calculations presented below are for | [7 empty] | Buildout |  |  |  | Phase |  | Phase #
Separate calculations must be provided for both current phase and buildout.
Step 1: Calculate Total Fixture Value
Fixture |  |  |  | Fixture Value (GPM @ 60psi) |  |  |  | No. of Fixtures |  |  |  | Fixture Value (GPM @ 60psi)
Bathroom Group |  |  |  | 12 |  |  | x |  |  |  | =
Bathtub |  |  |  | 8 |  |  | x | 41 |  |  | = | 328
Bedpan Washers |  |  |  | 10 |  |  | x |  |  |  | =
Bidet |  |  |  | 2 |  |  | x |  |  |  | =
Dental Unit |  |  |  | 2 |  |  | x |  |  |  | =
Dishwasher |  |  |  | 1.6 |  |  | x | 23 |  |  | = | 36.8
Drinking Fountain - Public |  |  |  | 2 |  |  | x |  |  |  | =
Hose Bibs (c/w 50 ft Wash Down) |  |  |  | 5 |  |  | x | 40 |  |  | = | 200
Kitchen Sink |  |  |  | 1.8 |  |  | x | 23 |  |  | = | 41.4
Lavatory |  |  |  | 1.5 |  |  | x | 77 |  |  | = | 115.5
Showerhead (Shower only) |  |  |  | 2.5 |  |  | x | 11 |  |  | = | 27.5
Service Sink |  |  |  | 4 |  |  | x |  |  |  | =
Toilet:
- Flush Valve |  |  |  | 24 |  |  | x |  |  |  | =
- Tank Type |  |  |  | 4 |  |  | x | 69 |  |  | = | 276
Urinal:
- Pedestal Flush Valve |  |  |  | 10 |  |  | x |  |  |  | =
- Wall Flush Valve |  |  |  | 10 |  |  | x |  |  |  | =
Wash Sink (Each Set of Faucets) |  |  |  | 4 |  |  | x |  |  |  | =
Washing Machine |  |  |  | 4 |  |  | x | 23 |  |  | = | 92
Other:
[7 empty] | x |  |  |  | =
[7 empty] | x |  |  |  | =
[7 empty] | x |  |  |  | =
Total Fixture Value | [10 empty] | = | 1117.2 |  |  | GPM |  | (A)
Page 2 of 2
Water Meter Sizing Calculation Sheet
For Non-Fire Service Meters
Methodology: AWWA M22
Step 2: Calculate Probable Peak Demand
Refer to Figure 4-2 or 4-3 | [9 empty] | Probable Peak Demand | = | 62 |  |  | GPM |  | (B)
Step 3: Apply Pressure Adjustment Factor
[10 empty] | Water System Pressure (Hydraulic Grade Line - Elevation) - max. 80psi | = | 60 |  |  | psi
[10 empty] | Pressure Factor from Table 4-1 | = | 1 |  |  |  |  | (C)
[10 empty] | Adjusted Peak Demand (B x C) | = | 62 |  |  | GPM |  | (D)
Step 4: Identify Irrigation Demand
[10 empty] | Total Irrigation Demand | = | 35 |  |  | GPM |  | (E)
Step 5: Confirm Design Demand
[10 empty] | Design Demand (Greater of D & E) | = | 62 |  |  | GPM |  | (F)
Step 6: Size and Select Water Meter
[7 empty] | Water Meter Make / Model: | = | Neptune Tru/Flo
[10 empty] | Water Meter Size | = | 2 |  |  | inch
[10 empty] | Meter Location (Outside / Inside) | = | Outside
Professional Certification
[5 empty] | Name: |  |  | Xiangyang Tan
[5 empty] | Company: |  |  | XT Engineering Ltd.
[5 empty] | Date: |  |  | 2020-12-07
Revision:
Comments:
Seal