## Sheet1
AvaCare Health
Clean Room Calculation
Address | 103-3568 191 St , Surrey,BC
ISO classfication | 8
Air Change Rate | 20
Room name | Length | Width | Height | Volume | ACH | Air flow | Diffuser amount | Each diffuser | Return | Return | Design Supply | Design Return
| ft | ft | ft | cu.ft. | # | CFM |  | CFM |  | CFM | CFM | CFM
Intergraded package line | 30 | 12 | 10 | 3600 | 20 | 1200 | 3 | 400 | 1 | 1080 | 1200 | 1080
In Progress Storage | 8 | 12 | 10 | 960 | 20 | 320 | 1 | 320 | 1 | 288 | 320 | 290
Process equipment room 2 | 9 | 12 | 10 | 1080 | 20 | 360 | 1 | 360 | 1 | 324 | 360 | 325
Cleaning area | 10 | 10 | 10 | 1000 | 20 | 333.3333 | 1 | 333.3333 | 1 | 300 | 335 | 300
Powder Blending Rm | 10 | 10 | 10 | 1000 | 20 | 333.3333 | 1 | 333.3333 | 1 | 300 | 335 | 300
Dispensing rm | 10 | 10 | 10 | 1000 | 20 | 333.3333 | 1 | 333.3333 | 1 | 300 | 335 | 300
Process equipment room 1 | 9 | 12 | 10 | 1080 | 20 | 360 | 1 | 360 | 1 | 324 | 360 | 325
Process equipment room 2 | 9 | 12 | 10 | 1080 | 20 | 360 | 1 | 360 | 1 | 324 | 360 | 325
Lab | 15 | 10 | 10 | 1500 | 20 | 500 | 2 | 250 | 1 | 450 | 500 | 450
Corridor | 54.6 | 5.7 | 10 | 3112.2 | 6 | 311.22 | 2 | 155.61 | 1 | 280.098 | 310 | 280
[5 empty] | Total | 4411.22 |  |  | Total | 3970.098