## Sheet1
PIPE SIZING/LOSS CALCULATION
Temp. Difference
|  | T supply | T return |  | DT
| C | 87.7 | 71.1 |  | 16.6
| F | 189.86 | 159.98 |  | 29.88
Section | Heating Load |  |  |  | Diametre d mm |  | length L m |  | Friction/m R Pa/m |  | Friction RxL Pa |  | Velocity V m/s | Head loss hw Pa | Fitting loss factor | Fitting loss Z=hw(Pa) |  | Total Loss RL+Z Pa
| W | MBH | kg/s | GPM |  | IN |  | FT |  | FT.Water/100FT |  | IN.Water |  |  |  |  | IN.Water |  | In.Water
1 | 234792 | 801.3379 | 3.261 | 51.6868 | 70 | 2.8 | 1 | 3.28 | 66.684 | 0.68013 | 66.684 | 0.26781 | 0.84735 | 352.9013 |  | 0 | 0 | 66.684 | 0.26781 | return main floor
2 | 223912 | 764.2048 | 3.1099 | 49.2917 | 70 | 2.8 |  | 0 | 60.8051 | 0.62017 | 0 | 0 | 0.80809 | 320.9529 |  | 0 | 0 | 0 | 0
3 | 222287 | 758.6587 | 3.0873 | 48.934 | 70 | 2.8 |  | 0 | 59.9502 | 0.61145 | 0 | 0 | 0.80222 | 316.3113 |  | 0 | 0 | 0 | 0
4 | 215882 | 736.7986 | 2.9984 | 47.524 | 70 | 2.8 |  | 0 | 56.6392 | 0.57768 | 0 | 0 | 0.77911 | 298.3455 |  | 0 | 0 | 0 | 0
5 | 206537 | 704.9044 | 2.8686 | 45.4668 | 70 | 2.8 |  | 0 | 51.9761 | 0.53012 | 0 | 0 | 0.74538 | 273.0753 |  | 0 | 0 | 0 | 0
6 | 201097 | 686.3379 | 2.793 | 44.2693 | 70 | 2.8 |  | 0 | 49.3532 | 0.50337 | 0 | 0 | 0.72575 | 258.8796 |  | 0 | 0 | 0 | 0
7 | 196397 | 670.2969 | 2.7277 | 43.2346 | 70 | 2.8 |  | 0 | 47.1414 | 0.48081 | 0 | 0 | 0.70879 | 246.92 |  | 0 | 0 | 0 | 0
8 | 186657 | 637.0546 | 2.5925 | 41.0905 | 70 | 2.8 |  | 0 | 42.7181 | 0.4357 | 0 | 0 | 0.67364 | 223.0361 |  | 0 | 0 | 0 | 0
9 | 181257 | 618.6246 | 2.5175 | 39.9017 | 70 | 2.8 |  | 0 | 40.359 | 0.41163 | 0 | 0 | 0.65415 | 210.3179 |  | 0 | 0 | 0 | 0
10 | 174952 | 597.1058 | 2.4299 | 38.5137 | 70 | 2.8 |  | 0 | 37.6886 | 0.3844 | 0 | 0 | 0.63139 | 195.9406 |  | 0 | 0 | 0 | 0
11 | 173112 | 590.8259 | 2.4043 | 38.1087 | 70 | 2.8 |  | 0 | 36.9264 | 0.37662 | 0 | 0 | 0.62475 | 191.8408 |  | 0 | 0 | 0 | 0
12 | 167672 | 572.2594 | 2.3288 | 36.9111 | 70 | 2.8 |  | 0 | 34.718 | 0.3541 | 0 | 0 | 0.60512 | 179.9731 |  | 0 | 0 | 0 | 0
13 | 163312 | 557.3788 | 2.2682 | 35.9513 | 70 | 2.8 |  | 0 | 32.9968 | 0.33655 | 0 | 0 | 0.58939 | 170.7351 |  | 0 | 0 | 0 | 0
14 | 157912 | 538.9488 | 2.1932 | 34.7626 | 70 | 2.8 |  | 0 | 30.9251 | 0.31542 | 0 | 0 | 0.5699 | 159.6309 |  | 0 | 0 | 0 | 0
15 | 153777 | 524.8362 | 2.1358 | 33.8523 | 70 | 2.8 |  | 0 | 29.3837 | 0.29969 | 0 | 0 | 0.55497 | 151.3803 |  | 0 | 0 | 0 | 0
16 | 149057 | 508.727 | 2.0702 | 32.8132 | 50 | 2 |  | 0 | 155.5398 | 1.5864 | 0 | 0 | 1.0544 | 546.391 |  | 0 | 0 | 0 | 0
17 | 130957 | 446.9522 | 1.8188 | 28.8287 | 50 | 2 |  | 0 | 120.8016 | 1.2321 | 0 | 0 | 0.92633 | 421.7511 |  | 0 | 0 | 0 | 0
18 | 112857 | 385.1775 | 1.5675 | 24.8442 | 50 | 2 |  | 0 | 90.4299 | 0.92232 | 0 | 0 | 0.7983 | 313.2245 |  | 0 | 0 | 0 | 0
19 | 109357 | 373.2321 | 1.5188 | 24.0737 | 50 | 2 |  | 0 | 85.0607 | 0.86756 | 0 | 0 | 0.77354 | 294.0979 |  | 0 | 0 | 0 | 0
20 | 106637 | 363.9488 | 1.4811 | 23.475 | 50 | 2 |  | 0 | 81.0009 | 0.82616 | 0 | 0 | 0.7543 | 279.6499 |  | 0 | 0 | 0 | 0
21 | 103237 | 352.3447 | 1.4338 | 22.7265 | 50 | 2 |  | 0 | 76.0649 | 0.77581 | 0 | 0 | 0.73025 | 262.1015 |  | 0 | 0 | 0 | 0
22 | 98237 | 335.2799 | 1.3644 | 21.6258 | 50 | 2 |  | 0 | 69.0861 | 0.70463 | 0 | 0 | 0.69488 | 237.328 |  | 0 | 0 | 0 | 0
23 | 92417 | 315.4164 | 1.2836 | 20.3446 | 50 | 2 |  | 0 | 61.3826 | 0.62606 | 0 | 0 | 0.65372 | 210.0402 |  | 0 | 0 | 0 | 0
24 | 89017 | 303.8123 | 1.2363 | 19.5961 | 40 | 1.6 |  | 0 | 179.5798 | 1.8316 | 0 | 0 | 0.98385 | 475.7565 |  | 0 | 0 | 0 | 0
25 | 85087 | 290.3993 | 1.1818 | 18.731 | 40 | 1.6 |  | 0 | 164.4343 | 1.6771 | 0 | 0 | 0.94042 | 434.6756 |  | 0 | 0 | 0 | 0
26 | 74655 | 254.7952 | 1.0369 | 16.4345 | 40 | 1.6 |  | 0 | 127.4533 | 1.2999 | 0 | 0 | 0.82512 | 334.6236 |  | 0 | 0 | 0 | 0
27 | 69385 | 236.8089 | 0.96368 | 15.2743 | 40 | 1.6 |  | 0 | 110.551 | 1.1275 | 0 | 0 | 0.76687 | 289.048 |  | 0 | 0 | 0 | 0
28 | 65985 | 225.2048 | 0.91646 | 14.5259 | 40 | 1.6 |  | 0 | 100.2804 | 1.0228 | 0 | 0 | 0.72929 | 261.4143 |  | 0 | 0 | 0 | 0
29 | 62925 | 214.7611 | 0.87396 | 13.8522 | 40 | 1.6 |  | 0 | 91.4621 | 0.93285 | 0 | 0 | 0.69547 | 237.7307 |  | 0 | 0 | 0 | 0
30 | 59525 | 203.157 | 0.82674 | 13.1038 | 40 | 1.6 |  | 0 | 82.1366 | 0.83774 | 0 | 0 | 0.6579 | 212.7344 |  | 0 | 0 | 0 | 0
30a | 52715 | 179.9147 | 0.73215 | 11.6046 | 32 | 1.28 |  | 0 | 203.9955 | 2.0806 | 0 | 0 | 0.91036 | 407.3308 |  | 0 | 0 | 0 | 0
31 | 51255 | 174.9317 | 0.71187 | 11.2832 | 32 | 1.28 |  | 0 | 193.1311 | 1.9698 | 0 | 0 | 0.88514 | 385.0803 |  | 0 | 0 | 0 | 0
32 | 44945 | 153.3959 | 0.62424 | 9.8941 | 32 | 1.28 |  | 0 | 149.5784 | 1.5256 | 0 | 0 | 0.77617 | 296.1022 |  | 0 | 0 | 0 | 0
33 | 43105 | 147.116 | 0.59868 | 9.4891 | 32 | 1.28 |  | 0 | 137.9192 | 1.4067 | 0 | 0 | 0.7444 | 272.3543 |  | 0 | 0 | 0 | 0
34 | 38905 | 132.7816 | 0.54035 | 8.5645 | 32 | 1.28 |  | 0 | 113.0668 | 1.1532 | 0 | 0 | 0.67187 | 221.8655 |  | 0 | 0 | 0 | 0
35 | 34705 | 118.4471 | 0.48201 | 7.6399 | 25 | 1 |  | 0 | 321.9332 | 3.2835 | 0 | 0 | 0.98195 | 473.9176 |  | 0 | 0 | 0 | 0
36 | 29305 | 100.0171 | 0.40701 | 6.4512 | 25 | 1 |  | 0 | 231.5422 | 2.3616 | 0 | 0 | 0.82916 | 337.9109 |  | 0 | 0 | 0 | 0
37 | 25285 | 86.2969 | 0.35118 | 5.5662 | 25 | 1 |  | 0 | 173.8559 | 1.7732 | 0 | 0 | 0.71542 | 251.5618 |  | 0 | 0 | 0 | 0
38 | 20585 | 70.256 | 0.2859 | 4.5316 | 20 | 0.8 |  | 0 | 366.8522 | 3.7416 | 0 | 0 | 0.91006 | 407.062 |  | 0 | 0 | 0 | 0
39 | 15205 | 51.8942 | 0.21118 | 3.3472 | 20 | 0.8 |  | 0 | 203.6633 | 2.0772 | 0 | 0 | 0.67221 | 222.0914 |  | 0 | 0 | 0 | 0
40 | 13000 | 44.3686 | 0.18056 | 2.8618 | 20 | 0.8 |  | 0 | 150.4736 | 1.5347 | 0 | 0 | 0.57473 | 162.3475 |  | 0 | 0 | 0 | 0
41 | 13000 | 44.3686 | 0.18056 | 2.8618 | 20 | 0.8 |  | 0 | 150.4736 | 1.5347 | 0 | 0 | 0.57473 | 162.3475 | 0 | 0 | 0 | 0 | 0
42 | 9750 | 33.2765 | 0.13542 | 2.1464 | 20 | 0.8 | 10 | 32.8 | 86.6041 | 0.8833 | 866.0406 | 3.4781 | 0.43104 | 91.3204 | 1 | 91.3204 | 0.36675 | 957.361 | 3.8448
43 | 6500 | 22.1843 | 0.090278 | 1.4309 | 20 | 0.8 | 11 | 36.08 | 40.0762 | 0.40875 | 440.8382 | 1.7704 | 0.28736 | 40.5869 | 2 | 81.1737 | 0.326 | 522.0119 | 2.0964
44 | 3250 | 11.0922 | 0.045139 | 0.71545 | 15 | 0.6 | 12 | 39.36 | 45.9899 | 0.46907 | 551.8783 | 2.2164 | 0.25543 | 32.0686 | 3 | 96.2059 | 0.38637 | 648.0842 | 2.6027
45 | 5440 | 18.5666 | 0.075556 | 1.1976 | 15 | 0.6 | 10 | 32.8 | 122.1702 | 1.2461 | 1221.7015 | 4.9064 | 0.42756 | 89.8486 | 1 | 89.8486 | 0.36084 | 1311.5502 | 5.2673 | Supply | Main Floor
46 | 8690 | 29.6587 | 0.12069 | 1.913 | 20 | 0.8 | 10 | 32.8 | 69.5206 | 0.70906 | 695.206 | 2.792 | 0.38418 | 72.5435 | 1 | 72.5435 | 0.29134 | 767.7495 | 3.0833
47 | 10315 | 35.2048 | 0.14326 | 2.2707 | 20 | 0.8 | 10 | 32.8 | 96.4635 | 0.98386 | 964.6349 | 3.874 | 0.45602 | 102.2109 | 1 | 102.2109 | 0.41049 | 1066.8458 | 4.2845
48 | 16720 | 57.0648 | 0.23222 | 3.6807 | 25 | 1 | 10 | 32.8 | 78.305 | 0.79866 | 783.0496 | 3.1448 | 0.47308 | 109.9996 | 1 | 109.9996 | 0.44177 | 893.0493 | 3.5865
49 | 26065 | 88.959 | 0.36201 | 5.7379 | 25 | 1 | 10 | 32.8 | 184.4077 | 1.8808 | 1844.0767 | 7.4059 | 0.73749 | 267.3217 | 1 | 267.3217 | 1.0736 | 2111.3984 | 8.4795
50 | 31505 | 107.5256 | 0.43757 | 6.9355 | 25 | 1 | 10 | 32.8 | 266.5828 | 2.719 | 2665.8277 | 10.7061 | 0.89141 | 390.551 | 1 | 390.551 | 1.5685 | 3056.3787 | 12.2746
51 | 36205 | 123.5666 | 0.50285 | 7.9701 | 32 | 1.28 | 10 | 32.8 | 98.3838 | 1.0034 | 983.8385 | 3.9512 | 0.62524 | 192.1392 | 1 | 192.1392 | 0.77164 | 1175.9777 | 4.7228
52 | 45947 | 156.8157 | 0.63815 | 10.1147 | 32 | 1.28 | 10 | 32.8 | 156.1252 | 1.5924 | 1561.2521 | 6.2701 | 0.79348 | 309.4519 | 1 | 309.4519 | 1.2428 | 1870.704 | 7.5129
53 | 51347 | 175.2457 | 0.71315 | 11.3035 | 32 | 1.28 | 10 | 32.8 | 193.8069 | 1.9767 | 1938.0695 | 7.7834 | 0.88673 | 386.464 | 1 | 386.464 | 1.5521 | 2324.5334 | 9.3355
54 | 57652 | 196.7645 | 0.80072 | 12.6914 | 32 | 1.28 | 10 | 32.8 | 242.925 | 2.4777 | 2429.2504 | 9.756 | 0.99562 | 487.2004 | 1 | 487.2004 | 1.9566 | 2916.4508 | 11.7127
55 | 59492 | 203.0444 | 0.82628 | 13.0965 | 32 | 1.28 | 10 | 32.8 | 258.2991 | 2.6345 | 2582.9911 | 10.3735 | 1.0274 | 518.7953 | 1 | 518.7953 | 2.0835 | 3101.7864 | 12.457
56 | 64932 | 221.6109 | 0.90183 | 14.2941 | 40 | 1.6 | 10 | 32.8 | 97.2004 | 0.99138 | 972.0043 | 3.9036 | 0.71766 | 253.1374 | 1 | 253.1374 | 1.0166 | 1225.1417 | 4.9202
57 | 69292 | 236.4915 | 0.96239 | 15.2539 | 40 | 1.6 | 10 | 32.8 | 110.2635 | 1.1246 | 1102.6348 | 4.4283 | 0.76584 | 288.2737 | 1 | 288.2737 | 1.1577 | 1390.9085 | 5.586
58 | 74692 | 254.9215 | 1.0374 | 16.4426 | 40 | 1.6 | 10 | 32.8 | 127.5762 | 1.3012 | 1275.7619 | 5.1235 | 0.82553 | 334.9554 | 1 | 334.9554 | 1.3452 | 1610.7173 | 6.4687
59 | 78827 | 269.0341 | 1.0948 | 17.3529 | 40 | 1.6 | 10 | 32.8 | 141.6812 | 1.4451 | 1416.8123 | 5.69 | 0.87123 | 373.0687 | 1 | 373.0687 | 1.4983 | 1789.881 | 7.1883
60 | 83547 | 285.1433 | 1.1604 | 18.3919 | 40 | 1.6 | 10 | 32.8 | 158.6806 | 1.6184 | 1586.8061 | 6.3727 | 0.9234 | 419.0835 | 1 | 419.0835 | 1.6831 | 2005.8896 | 8.0558
61 | 101647 | 346.9181 | 1.4118 | 22.3765 | 40 | 1.6 | 10 | 32.8 | 232.7502 | 2.3739 | 2327.5025 | 9.3474 | 1.1234 | 620.3374 | 1 | 620.3374 | 2.4913 | 2947.8399 | 11.8387
62 | 119747 | 408.6928 | 1.6632 | 26.361 | 50 | 2 | 10 | 32.8 | 101.4765 | 1.035 | 1014.765 | 4.0754 | 0.84704 | 352.6371 | 1 | 352.6371 | 1.4162 | 1367.4021 | 5.4916
63 | 123247 | 420.6382 | 1.7118 | 27.1315 | 50 | 2 | 10 | 32.8 | 107.3304 | 1.0947 | 1073.3038 | 4.3105 | 0.87179 | 373.5524 | 1 | 373.5524 | 1.5002 | 1446.8561 | 5.8107
64 | 125967 | 429.9215 | 1.7495 | 27.7302 | 50 | 2 | 10 | 32.8 | 111.9924 | 1.1422 | 1119.9243 | 4.4977 | 0.89103 | 390.2225 | 1 | 390.2225 | 1.5672 | 1510.1468 | 6.0648
65 | 129367 | 441.5256 | 1.7968 | 28.4787 | 50 | 2 | 10 | 32.8 | 117.9587 | 1.2031 | 1179.5867 | 4.7373 | 0.91508 | 411.572 | 1 | 411.572 | 1.6529 | 1591.1586 | 6.3902
66 | 134367 | 458.5904 | 1.8662 | 29.5794 | 50 | 2 | 10 | 32.8 | 127.0124 | 1.2954 | 1270.1243 | 5.1009 | 0.95045 | 444.0011 | 1 | 444.0011 | 1.7831 | 1714.1254 | 6.884
67 | 140187 | 478.4539 | 1.947 | 30.8606 | 50 | 2 | 10 | 32.8 | 137.9706 | 1.4072 | 1379.7064 | 5.541 | 0.99162 | 483.2972 | 1 | 483.2972 | 1.941 | 1863.0036 | 7.4819
68 | 143587 | 490.058 | 1.9943 | 31.6091 | 50 | 2 | 10 | 32.8 | 144.5812 | 1.4746 | 1445.8123 | 5.8065 | 1.0157 | 507.0246 | 1 | 507.0246 | 2.0362 | 1952.8369 | 7.8427
69 | 147517 | 503.471 | 2.0488 | 32.4742 | 50 | 2 | 10 | 32.8 | 152.4142 | 1.5545 | 1524.1424 | 6.1211 | 1.0435 | 535.1591 | 1 | 535.1591 | 2.1492 | 2059.3015 | 8.2703
70 | 157949 | 539.0751 | 2.1937 | 34.7707 | 50 | 2 | 10 | 32.8 | 174.2049 | 1.7768 | 1742.0486 | 6.9962 | 1.1173 | 613.5254 | 1 | 613.5254 | 2.464 | 2355.5739 | 9.4601
71 | 163219 | 557.0614 | 2.2669 | 35.9308 | 50 | 2 | 10 | 32.8 | 185.7643 | 1.8947 | 1857.6429 | 7.4604 | 1.1545 | 655.1492 | 1 | 655.1492 | 2.6311 | 2512.792 | 10.0915
72 | 177219 | 604.843 | 2.4614 | 39.0128 | 50 | 2 | 10 | 32.8 | 218.2698 | 2.2262 | 2182.698 | 8.7659 | 1.2536 | 772.3592 | 1 | 772.3592 | 3.1018 | 2955.0572 | 11.8677
73 | 180279 | 615.2867 | 2.5039 | 39.6864 | 50 | 2 | 10 | 32.8 | 225.7224 | 2.3022 | 2257.2236 | 9.0652 | 1.2752 | 799.2618 | 1 | 799.2618 | 3.2099 | 3056.4854 | 12.275
74 | 183679 | 626.8908 | 2.5511 | 40.4349 | 50 | 2 | 10 | 32.8 | 234.1493 | 2.3882 | 2341.493 | 9.4036 | 1.2993 | 829.6937 | 1 | 829.6937 | 3.3321 | 3171.1867 | 12.7357
75 | 190489 | 650.1331 | 2.6457 | 41.934 | 50 | 2 | 10 | 32.8 | 251.4912 | 2.565 | 2514.9117 | 10.1 | 1.3474 | 892.3569 | 1 | 892.3569 | 3.5838 | 3407.2686 | 13.6838
76 | 191949 | 655.116 | 2.666 | 42.2554 | 50 | 2 | 10 | 32.8 | 255.2895 | 2.6038 | 2552.8954 | 10.2526 | 1.3578 | 906.0882 | 1 | 906.0882 | 3.6389 | 3458.9836 | 13.8915
77 | 198259 | 676.6519 | 2.7536 | 43.6445 | 70 | 2.8 | 10 | 32.8 | 48.0116 | 0.48969 | 480.1163 | 1.9282 | 0.71551 | 251.6242 | 1 | 251.6242 | 1.0105 | 731.7405 | 2.9387
78 | 200099 | 682.9317 | 2.7792 | 44.0496 | 70 | 2.8 | 10 | 32.8 | 48.8793 | 0.49854 | 488.7933 | 1.963 | 0.72215 | 256.3164 | 1 | 256.3164 | 1.0294 | 745.1097 | 2.9924
79 | 201939 | 689.2116 | 2.8047 | 44.4546 | 70 | 2.8 | 10 | 32.8 | 49.7548 | 0.50747 | 497.5475 | 1.9982 | 0.72879 | 261.052 | 1 | 261.052 | 1.0484 | 758.5995 | 3.0466
80 | 206139 | 703.5461 | 2.863 | 45.3792 | 70 | 2.8 | 10 | 32.8 | 51.7819 | 0.52814 | 517.819 | 2.0796 | 0.74395 | 272.0238 | 1 | 272.0238 | 1.0925 | 789.8429 | 3.1721
81 | 211539 | 721.9761 | 2.938 | 46.568 | 70 | 2.8 | 10 | 32.8 | 54.4473 | 0.55533 | 544.4731 | 2.1866 | 0.76343 | 286.4623 | 1 | 286.4623 | 1.1505 | 830.9355 | 3.3371
82 | 220259 | 751.7372 | 3.0592 | 48.4876 | 70 | 2.8 | 10 | 32.8 | 58.8918 | 0.60066 | 588.9176 | 2.3651 | 0.7949 | 310.566 | 1 | 310.566 | 1.2473 | 899.4836 | 3.6124
83 | 224959 | 767.7782 | 3.1244 | 49.5222 | 70 | 2.8 | 10 | 32.8 | 61.3591 | 0.62582 | 613.5914 | 2.4642 | 0.81187 | 323.9615 | 1 | 323.9615 | 1.3011 | 937.5529 | 3.7653
84 | 230339 | 786.1399 | 3.1992 | 50.7066 | 70 | 2.8 | 10 | 32.8 | 64.2453 | 0.65526 | 642.4529 | 2.5801 | 0.83128 | 339.6421 | 1 | 339.6421 | 1.364 | 982.0951 | 3.9442
85 | 232544 | 793.6655 | 3.2298 | 51.192 | 70 | 2.8 | 10 | 32.8 | 65.4472 | 0.66752 | 654.4724 | 2.6284 | 0.83924 | 346.176 | 1 | 346.176 | 1.3903 | 1000.6483 | 4.0187
86 | 237419 | 810.3038 | 3.2975 | 52.2652 | 70 | 2.8 | 10 | 32.8 | 68.1439 | 0.69502 | 681.4393 | 2.7367 | 0.85683 | 360.8424 | 1 | 360.8424 | 1.4492 | 1042.2817 | 4.1859
87 | 240669 | 821.3959 | 3.3426 | 52.9806 | 70 | 2.8 | 10 | 32.8 | 69.9718 | 0.71367 | 699.718 | 2.8101 | 0.86856 | 370.7891 | 1 | 370.7891 | 1.4891 | 1070.5071 | 4.2992
88 | 243919 | 832.4881 | 3.3878 | 53.6961 | 70 | 2.8 | 10 | 32.8 | 71.8237 | 0.73255 | 718.2374 | 2.8845 | 0.88029 | 380.871 | 1 | 380.871 | 1.5296 | 1099.1084 | 4.4141
89 | 247169 | 843.5802 | 3.4329 | 54.4115 | 70 | 2.8 | 10 | 32.8 | 73.6998 | 0.75169 | 736.9975 | 2.9598 | 0.89202 | 391.0881 | 1 | 391.0881 | 1.5706 | 1128.0856 | 4.5305
1 | 4927 | 16.8157 | 0.068431 | 1.0846 | 20 | 0.8 |  | 0 | 23.8078 | 0.24282 | 0 | 0 | 0.21782 | 23.3198 |  | 0 | 0 | 0 | 0 | Second Floor Supply
2 | 8383 | 28.6109 | 0.11643 | 1.8454 | 20 | 0.8 |  | 0 | 64.9175 | 0.66212 | 0 | 0 | 0.37061 | 67.5084 |  | 0 | 0 | 0 | 0
3 | 10010 | 34.1638 | 0.13903 | 2.2036 | 20 | 0.8 |  | 0 | 91.0761 | 0.92892 | 0 | 0 | 0.44254 | 96.2558 |  | 0 | 0 | 0 | 0
4 | 15450 | 52.7304 | 0.21458 | 3.4011 | 25 | 1 |  | 0 | 67.3095 | 0.68651 | 0 | 0 | 0.43715 | 93.9238 |  | 0 | 0 | 0 | 0
5 | 20150 | 68.7713 | 0.27986 | 4.4358 | 25 | 1 |  | 0 | 112.098 | 1.1433 | 0 | 0 | 0.57013 | 159.7603 |  | 0 | 0 | 0 | 0
6 | 26810 | 91.5017 | 0.37236 | 5.9019 | 25 | 1 |  | 0 | 194.7742 | 1.9866 | 0 | 0 | 0.75857 | 282.8215 |  | 0 | 0 | 0 | 0
7 | 32685 | 111.5529 | 0.45396 | 7.1952 | 32 | 1.28 |  | 0 | 80.7623 | 0.82372 | 0 | 0 | 0.56445 | 156.5943 |  | 0 | 0 | 0 | 0
8 | 34525 | 117.8328 | 0.47951 | 7.6003 | 32 | 1.28 |  | 0 | 89.7588 | 0.91548 | 0 | 0 | 0.59623 | 174.7215 |  | 0 | 0 | 0 | 0
9 | 39705 | 135.5119 | 0.55146 | 8.7406 | 32 | 1.28 |  | 0 | 117.6118 | 1.1996 | 0 | 0 | 0.68568 | 231.0837 |  | 0 | 0 | 0 | 0
10 | 44205 | 150.8703 | 0.61396 | 9.7312 | 32 | 1.28 |  | 0 | 144.8328 | 1.4772 | 0 | 0 | 0.76339 | 286.4321 |  | 0 | 0 | 0 | 0
11 | 48510 | 165.5631 | 0.67375 | 10.6789 | 32 | 1.28 |  | 0 | 173.5055 | 1.7696 | 0 | 0 | 0.83774 | 344.9383 |  | 0 | 0 | 0 | 0
12 | 49980 | 170.5802 | 0.69417 | 11.0025 | 32 | 1.28 |  | 0 | 183.8853 | 1.8755 | 0 | 0 | 0.86313 | 366.1604 |  | 0 | 0 | 0 | 0
13 | 54410 | 185.6997 | 0.75569 | 11.9778 | 32 | 1.28 |  | 0 | 216.9797 | 2.213 | 0 | 0 | 0.93963 | 433.9466 |  | 0 | 0 | 0 | 0
14 | 59280 | 202.3208 | 0.82333 | 13.0498 | 40 | 1.6 |  | 0 | 81.4839 | 0.83108 | 0 | 0 | 0.65519 | 210.9868 |  | 0 | 0 | 0 | 0
15 | 69044 | 235.6451 | 0.95894 | 15.1993 | 40 | 1.6 |  | 0 | 109.4985 | 1.1168 | 0 | 0 | 0.7631 | 286.2139 |  | 0 | 0 | 0 | 0
15a | 71648 | 244.5324 | 0.99511 | 15.7725 | 41 | 1.64 |  | 0 | 103.6524 | 1.0572 | 0 | 0 | 0.75373 | 279.2232 |  | 0 | 0 | 0 | 0
16 | 74484 | 254.2116 | 1.0345 | 16.3968 | 40 | 1.6 |  | 0 | 126.8861 | 1.2942 | 0 | 0 | 0.82323 | 333.0925 |  | 0 | 0 | 0 | 0
17 | 78304 | 267.2491 | 1.0876 | 17.2378 | 40 | 1.6 |  | 0 | 139.8566 | 1.4264 | 0 | 0 | 0.86545 | 368.1347 |  | 0 | 0 | 0 | 0
18 | 83744 | 285.8157 | 1.1631 | 18.4353 | 40 | 1.6 |  | 0 | 159.411 | 1.6259 | 0 | 0 | 0.92557 | 421.0622 |  | 0 | 0 | 0 | 0
19 | 89014 | 303.802 | 1.2363 | 19.5954 | 40 | 1.6 |  | 0 | 179.5679 | 1.8315 | 0 | 0 | 0.98382 | 475.7244 |  | 0 | 0 | 0 | 0
20 | 94284 | 321.7884 | 1.3095 | 20.7556 | 50 | 2 |  | 0 | 63.8046 | 0.65076 | 0 | 0 | 0.66692 | 218.6124 |  | 0 | 0 | 0 | 0
21 | 99554 | 339.7747 | 1.3827 | 21.9157 | 50 | 2 |  | 0 | 70.892 | 0.72305 | 0 | 0 | 0.7042 | 243.734 |  | 0 | 0 | 0 | 0
22 | 104824 | 357.7611 | 1.4559 | 23.0758 | 50 | 2 |  | 0 | 78.3497 | 0.79911 | 0 | 0 | 0.74148 | 270.2217 |  | 0 | 0 | 0 | 0
23 | 110644 | 377.6246 | 1.5367 | 24.357 | 50 | 2 |  | 0 | 87.0161 | 0.88751 | 0 | 0 | 0.78265 | 301.061 |  | 0 | 0 | 0 | 0
24 | 112414 | 383.6655 | 1.5613 | 24.7467 | 50 | 2 |  | 0 | 89.7412 | 0.9153 | 0 | 0 | 0.79517 | 310.7703 |  | 0 | 0 | 0 | 0
25 | 114184 | 389.7065 | 1.5859 | 25.1363 | 50 | 2 |  | 0 | 92.5082 | 0.94352 | 0 | 0 | 0.80769 | 320.6338 |  | 0 | 0 | 0 | 0
26 | 118524 | 404.5188 | 1.6462 | 26.0917 | 50 | 2 |  | 0 | 99.4695 | 1.0145 | 0 | 0 | 0.83839 | 345.4708 |  | 0 | 0 | 0 | 0
27 | 130884 | 446.7031 | 1.8178 | 28.8127 | 50 | 2 |  | 0 | 120.6704 | 1.2308 | 0 | 0 | 0.92581 | 421.281 |  | 0 | 0 | 0 | 0
28 | 133054 | 454.1092 | 1.848 | 29.2904 | 50 | 2 |  | 0 | 124.6027 | 1.2709 | 0 | 0 | 0.94116 | 435.3661 |  | 0 | 0 | 0 | 0
29 | 138814 | 473.7679 | 1.928 | 30.5584 | 70 | 2.8 |  | 0 | 24.132 | 0.24613 | 0 | 0 | 0.50097 | 123.354 |  | 0 | 0 | 0 | 0
30 | 140984 | 481.1741 | 1.9581 | 31.0361 | 70 | 2.8 |  | 0 | 24.8619 | 0.25357 | 0 | 0 | 0.50881 | 127.2408 |  | 0 | 0 | 0 | 0
31 | 145684 | 497.215 | 2.0234 | 32.0707 | 70 | 2.8 |  | 0 | 26.4798 | 0.27008 | 0 | 0 | 0.52577 | 135.8659 |  | 0 | 0 | 0 | 0
32 | 150384 | 513.256 | 2.0887 | 33.1054 | 70 | 2.8 |  | 0 | 28.148 | 0.28709 | 0 | 0 | 0.54273 | 144.7738 |  | 0 | 0 | 0 | 0
33 | 151252 | 516.2184 | 2.1007 | 33.2964 | 70 | 2.8 |  | 0 | 28.4616 | 0.29029 | 0 | 0 | 0.54586 | 146.4498 |  | 0 | 0 | 0 | 0
34 | 152120 | 519.1809 | 2.1128 | 33.4875 | 70 | 2.8 |  | 0 | 28.777 | 0.29351 | 0 | 0 | 0.54899 | 148.1355 |  | 0 | 0 | 0 | 0
35 | 171620 | 585.7338 | 2.3836 | 37.7802 | 70 | 2.8 |  | 0 | 36.314 | 0.37038 | 0 | 0 | 0.61937 | 188.5482 |  | 0 | 0 | 0 | 0
35a | 176320 | 601.7747 | 2.4489 | 38.8149 | 70 | 2.8 |  | 0 | 38.2603 | 0.39023 | 0 | 0 | 0.63633 | 199.0168 |  | 0 | 0 | 0 | 0
36 | 6500 | 22.1843 | 0.090278 | 1.4309 | 20 | 0.8 |  | 0 | 40.0762 | 0.40875 | 0 | 0 | 0.28736 | 40.5869 |  | 0 | 0 | 0 | 0 | second floor return
37 | 13000 | 44.3686 | 0.18056 | 2.8618 | 25 | 1 |  | 0 | 48.416 | 0.49381 | 0 | 0 | 0.36782 | 66.4975 |  | 0 | 0 | 0 | 0
38 | 19500 | 66.5529 | 0.27083 | 4.2927 | 32 | 1.28 |  | 0 | 30.0699 | 0.30669 | 0 | 0 | 0.33675 | 55.7376 |  | 0 | 0 | 0 | 0
39 | 24200 | 82.5939 | 0.33611 | 5.3274 | 32 | 1.28 |  | 0 | 45.3647 | 0.46269 | 0 | 0 | 0.41792 | 85.8439 |  | 0 | 0 | 0 | 0
40 | 25068 | 85.5563 | 0.34817 | 5.5184 | 32 | 1.28 |  | 0 | 48.526 | 0.49493 | 0 | 0 | 0.43291 | 92.1124 |  | 0 | 0 | 0 | 0
41 | 25936 | 88.5188 | 0.36022 | 5.7095 | 32 | 1.28 |  | 0 | 51.7921 | 0.52825 | 0 | 0 | 0.4479 | 98.6018 |  | 0 | 0 | 0 | 0
42 | 30636 | 104.5597 | 0.4255 | 6.7442 | 32 | 1.28 |  | 0 | 71.2975 | 0.72719 | 0 | 0 | 0.52907 | 137.5761 |  | 0 | 0 | 0 | 0
43 | 35336 | 120.6007 | 0.49078 | 7.7788 | 32 | 1.28 |  | 0 | 93.8735 | 0.95745 | 0 | 0 | 0.61023 | 183.0264 |  | 0 | 0 | 0 | 0
44 | 37506 | 128.0068 | 0.52092 | 8.2565 | 32 | 1.28 |  | 0 | 105.3325 | 1.0743 | 0 | 0 | 0.64771 | 206.1961 |  | 0 | 0 | 0 | 0
45 | 43266 | 147.6655 | 0.60092 | 9.5245 | 40 | 1.6 |  | 0 | 44.4219 | 0.45307 | 0 | 0 | 0.47819 | 112.3912 |  | 0 | 0 | 0 | 0
46 | 45436 | 155.0717 | 0.63106 | 10.0022 | 40 | 1.6 |  | 0 | 48.797 | 0.4977 | 0 | 0 | 0.50218 | 123.9478 |  | 0 | 0 | 0 | 0
47 | 57796 | 197.256 | 0.80272 | 12.7231 | 40 | 1.6 |  | 0 | 77.5852 | 0.79132 | 0 | 0 | 0.63879 | 200.5554 |  | 0 | 0 | 0 | 0
48 | 58447 | 199.4778 | 0.81176 | 12.8665 | 40 | 1.6 |  | 0 | 79.2838 | 0.80864 | 0 | 0 | 0.64598 | 205.0989 |  | 0 | 0 | 0 | 0
49 | 62787 | 214.2901 | 0.87204 | 13.8219 | 40 | 1.6 |  | 0 | 91.0739 | 0.92889 | 0 | 0 | 0.69395 | 236.6891 |  | 0 | 0 | 0 | 0
50 | 64557 | 220.3311 | 0.89662 | 14.2115 | 40 | 1.6 |  | 0 | 96.1151 | 0.98031 | 0 | 0 | 0.71351 | 250.222 |  | 0 | 0 | 0 | 0
51 | 66327 | 226.372 | 0.92121 | 14.6012 | 40 | 1.6 |  | 0 | 101.291 | 1.0331 | 0 | 0 | 0.73307 | 264.1311 |  | 0 | 0 | 0 | 0
52 | 72147 | 246.2355 | 1.002 | 15.8824 | 40 | 1.6 |  | 0 | 119.2605 | 1.2164 | 0 | 0 | 0.7974 | 312.5182 |  | 0 | 0 | 0 | 0
53 | 77417 | 264.2218 | 1.0752 | 17.0425 | 40 | 1.6 |  | 0 | 136.7889 | 1.3952 | 0 | 0 | 0.85565 | 359.8417 |  | 0 | 0 | 0 | 0
54 | 82687 | 282.2082 | 1.1484 | 18.2026 | 40 | 1.6 |  | 0 | 155.5119 | 1.5861 | 0 | 0 | 0.91389 | 410.5001 |  | 0 | 0 | 0 | 0
55 | 87957 | 300.1945 | 1.2216 | 19.3628 | 40 | 1.6 |  | 0 | 175.4293 | 1.7893 | 0 | 0 | 0.97214 | 464.4935 |  | 0 | 0 | 0 | 0
56 | 93227 | 318.1809 | 1.2948 | 20.5229 | 50 | 2 |  | 0 | 62.4277 | 0.63672 | 0 | 0 | 0.65945 | 213.7382 |  | 0 | 0 | 0 | 0
57 | 98667 | 336.7474 | 1.3704 | 21.7204 | 50 | 2 |  | 0 | 69.6732 | 0.71062 | 0 | 0 | 0.69793 | 239.4102 |  | 0 | 0 | 0 | 0
58 | 102487 | 349.785 | 1.4234 | 22.5614 | 50 | 2 |  | 0 | 74.9968 | 0.76492 | 0 | 0 | 0.72495 | 258.3071 |  | 0 | 0 | 0 | 0
59 | 107927 | 368.3515 | 1.499 | 23.7589 | 50 | 2 |  | 0 | 82.9141 | 0.84567 | 0 | 0 | 0.76343 | 286.4567 |  | 0 | 0 | 0 | 0
60 | 110531 | 377.2389 | 1.5352 | 24.3322 | 50 | 2 |  | 0 | 86.8435 | 0.88575 | 0 | 0 | 0.78185 | 300.4464 |  | 0 | 0 | 0 | 0
61 | 120295 | 410.5631 | 1.6708 | 26.4816 | 50 | 2 |  | 0 | 102.3823 | 1.0442 | 0 | 0 | 0.85091 | 355.8721 |  | 0 | 0 | 0 | 0
62 | 125165 | 427.1843 | 1.7384 | 27.5537 | 50 | 2 |  | 0 | 110.6076 | 1.1281 | 0 | 0 | 0.88536 | 385.2694 |  | 0 | 0 | 0 | 0
63 | 129595 | 442.3038 | 1.7999 | 28.5289 | 50 | 2 |  | 0 | 118.3643 | 1.2072 | 0 | 0 | 0.9167 | 413.024 |  | 0 | 0 | 0 | 0
64 | 131065 | 447.3208 | 1.8203 | 28.8525 | 50 | 2 |  | 0 | 120.996 | 1.2341 | 0 | 0 | 0.9271 | 422.447 |  | 0 | 0 | 0 | 0
65 | 135370 | 462.0137 | 1.8801 | 29.8002 | 50 | 2 |  | 0 | 128.8687 | 1.3144 | 0 | 0 | 0.95755 | 450.6544 |  | 0 | 0 | 0 | 0
66 | 139870 | 477.372 | 1.9426 | 30.7908 | 50 | 2 |  | 0 | 137.3622 | 1.401 | 0 | 0 | 0.98938 | 481.1139 |  | 0 | 0 | 0 | 0
67 | 145050 | 495.0512 | 2.0146 | 31.9311 | 70 | 2.8 |  | 0 | 26.2586 | 0.26782 | 0 | 0 | 0.52348 | 134.6859 |  | 0 | 0 | 0 | 0
68 | 146890 | 501.3311 | 2.0401 | 32.3362 | 70 | 2.8 |  | 0 | 26.903 | 0.27439 | 0 | 0 | 0.53012 | 138.1246 |  | 0 | 0 | 0 | 0
69 | 152765 | 521.3823 | 2.1217 | 33.6295 | 70 | 2.8 |  | 0 | 29.0124 | 0.29591 | 0 | 0 | 0.55132 | 149.3944 |  | 0 | 0 | 0 | 0
70 | 159425 | 544.1126 | 2.2142 | 35.0956 | 70 | 2.8 |  | 0 | 31.4989 | 0.32127 | 0 | 0 | 0.57536 | 162.7045 |  | 0 | 0 | 0 | 0
71 | 164125 | 560.1536 | 2.2795 | 36.1303 | 70 | 2.8 |  | 0 | 33.3145 | 0.33979 | 0 | 0 | 0.59232 | 172.4392 |  | 0 | 0 | 0 | 0
72 | 169565 | 578.7201 | 2.3551 | 37.3279 | 70 | 2.8 |  | 0 | 35.4788 | 0.36186 | 0 | 0 | 0.61195 | 184.0598 |  | 0 | 0 | 0 | 0
73 | 171192 | 584.273 | 2.3777 | 37.686 | 70 | 2.8 |  | 0 | 36.1392 | 0.3686 | 0 | 0 | 0.61782 | 187.6089 |  | 0 | 0 | 0 | 0
74 | 174648 | 596.0683 | 2.4257 | 38.4468 | 70 | 2.8 |  | 0 | 37.5621 | 0.38311 | 0 | 0 | 0.6303 | 195.2603 |  | 0 | 0 | 0 | 0
75 | 179575 | 612.884 | 2.4941 | 39.5314 | 70 | 2.8 |  | 0 | 39.6377 | 0.40428 | 0 | 0 | 0.64808 | 206.4326 |  | 0 | 0 | 0 | 0
Loop | [17 empty] | 0
0
0
[15 empty] | Friction Loss |  |  | #REF!

## Sheet2
| 给水卫生器具名称及卫生器具数 |  |  |  |  | 当量 | 流量 | 管经 | 流速 | 单位 | 管道 | 沿程
管段 | 马桶 | 小便器 | 洗脸盆 | 洗槽 | 洗涤盆 | 总数 | Qg | dj | V | 水头 | 长度 | 水头 | 备 注
编号 | 6 | 0.5 | 1 | 1 | 1 | ∑Ng | （L/s） | （mm） | （m/s） | i（mm/m） | （m） | hg（mm）
~1 | 1 | 0 | 0 | 0 | 0 | 6 | 1.6899 | 27 | 2.953 | 340.6552 | 2.7 | 919.7689 | 1、 qg=a*0.2√Ng+KNg
1~2 | 2 | 0 | 0 | 0 | 0 | 12 | 1.8928 | 43 | 1.3041 | 45.1684 | 1 | 45.1684 | 2、 局部水头取25%
2~3 | 3 | 0 | 0 | 0 | 0 | 18 | 2.0485 | 43 | 1.4114 | 51.9686 | 1 | 51.9686 | 3、 总水头h2=1.25*hg
3~4 | 4 | 0 | 0 | 0 | 0 | 24 | 2.1798 | 43 | 1.5018 | 58.022 | 0.7 | 40.6154 | 1.25*2.881=3.60m
4~5 | 4 | 3 | 0 | 0 | 0 | 25.5 | 2.21 | 43 | 1.5226 | 59.4535 | 2.5 | 148.6337 | 4、 水表水头损失：
5~6 | 4 | 3 | 1 | 0 | 0 | 26.5 | 2.2296 | 43 | 1.5361 | 60.3927 | 1 | 60.3927 | h3=2.5m
6~7 | 4 | 3 | 2 | 0 | 0 | 27.5 | 2.2488 | 43 | 1.5493 | 61.3206 | 5 | 306.6031 | 几何高度：h1=20m
7~8 | 8 | 6 | 4 | 0 | 0 | 55 | 2.6832 | 43 | 1.8486 | 83.8851 | 3.9 | 327.1517 | 流出水头：h4=2.5
8~9 | 12 | 9 | 6 | 0 | 0 | 82.5 | 3.0166 | 55 | 1.2703 | 31.8854 | 22 | 701.4783 | 5、 总水压：
9~10 | 24 | 9 | 12 | 0 | 0 | 160.5 | 3.7338 | 55 | 1.5724 | 46.55 | 6 | 279.3001 | H=h1+h2+h3+h4
10~11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 4.2 | 0 | 28.6m
11~12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 5 | 0
12~13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 13 | 0 | 6、计算管经为内经
13~14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | （取自《建筑给水排水设计
14~15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 手册》982页）
15~16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0
2881.0808
| 给水卫生器具名称及卫生器具数 |  |  |  |  | 当量 | 流量 | 管经 | 流速 | 单位 | 管道 | 沿程
管段 | 马桶 | 小便器 | 洗脸盆 | 洗槽 | 洗涤盆 | 总数 | Qg | dj | V | 水头 | 长度 | 水头
编号 | 6 | 0.5 | 1 | 1 | 1 | ∑Ng | （L/s） | （mm） | （m/s） | i（mm/m） | （m） | hg（mm）
~1‘ | 1 | 0 | 0 | 0 | 0 | 6 | 1.6899 | 27 | 2.953 | 340.6552 | 2.7 | 919.7689
1’~2‘ | 2 | 0 | 0 | 0 | 0 | 12 | 1.8928 | 43 | 1.3041 | 45.1684 | 1 | 45.1684
2’~3‘ | 3 | 0 | 0 | 0 | 0 | 18 | 2.0485 | 43 | 1.4114 | 51.9686 | 1 | 51.9686
3’~4‘ | 4 | 0 | 0 | 0 | 0 | 24 | 2.1798 | 43 | 1.5018 | 58.022 | 3.2 | 185.6703
4’~5‘ | 4 | 0 | 1 | 0 | 0 | 25 | 2.2 | 55 | 0.92646 | 18.2133 | 1 | 18.2133
5’~6‘ | 4 | 0 | 2 | 0 | 0 | 26 | 2.2198 | 55 | 0.9348 | 18.5051 | 5 | 92.5256
6’~7‘ | 8 | 0 | 4 | 0 | 0 | 52 | 2.6422 | 55 | 1.1127 | 25.2059 | 3.9 | 98.3031
7’~9 | 12 | 0 | 6 | 0 | 0 | 78 | 2.9664 | 55 | 1.2492 | 30.9494 | 41 | 1268.9268
2680.5449
用水量：
|  | q | n | k | T | Q
|  | l/人 | 人 |  | h | m3/h
|  | 50 | 120 | 2.5 | 10 | 1.5

## Sheet3
1、水枪的充实水注长度(450)、消火栓保护半径、消火栓布置间距：
H1(m) | H2(m) | SK(m) | Ld(m) | Ls(m) | R（m） | b(m) | S2(m)
4.5 | 1 | 4.1133 | 20 | 2.9204 | 22.9204 | 15 | 17.3305
2、消火栓栓口所需水压(mH2O)、校核流量：(最小流量2.5L/s、充实水柱≥7mH2O)
Sk' | qxh(L/S) | hd(mH2O) | Hq(mH2O) | Hxh(mH2O)
7 | 3.8 | 1.5523 | 9.1566 | 10.7089
3、几何高差(m)：H=20
4、管道水力计算：
管段 | Q(L/S) | di(mm) | ν(m/s) | 1000i | L(m) | 沿程hy | 管损Hg
1~2' | 3.8 | 105 | 0.43886 | 4.5622 | 4 | 0.018249 | 0.020074
2'~2 | 7.6 | 105 | 0.87772 | 16.1687 | 18 | 0.29104 | 0.32014
3~4 | 7.6 | 105 | 0.87772 | 16.1687 | 19 | 0.30721 | 0.33793
4~5 | 7.6 | 105 | 0.87772 | 16.1687 | 18 | 0.29104 | 0.32014
5~6 | 7.6 | 105 | 0.87772 | 16.1687 | 12 | 0.19402 | 0.21343
1.2117
5、入户水压(mH2O)： |  |  | 31.9206