## Sheet1
SWAY BRACING CALCAUTION
developped by Xiangyang Tan, P.Eng
|  | Location | Vancouver
| Spectural Acceleration | Ss | 1.5 | g | Vancvouer Ss=0.9, Cp=0.5
| Adjusted system weight | Cp | 0.7 |  | from Table 9.3.5.6.2
| Nipple height | Hr | 48 | inch
| Pipe length | L | 94 | ft
| Pipe size | Pipe size | 2 | inch
| Pipe type | Type | Schedule 10
| Pipe weight | Weight | 4.22 | lb/ft | from Table A9.3.5.6
| Amplifier factor | A | 15%
| Pipe Weigth after adjustment | Wp | 456.182 | lb
| Pipe modulus | S | 0.42 | in^3 | from table 9.1.1.6.1
| Nipple Strength | F | 36494.56 | PSI
| Note | F should be less than 30000 for steel pipe, 8000 PSI for CPVC pipe. Otherwise, additional longtigutle sway bracing should be added.
Sway Bracing
| Diameter in | Type | Length ft | Weight lb per ft | Weight lb
| 6 | Schedule 10 | 21 | 23.03 | 483.63
| 4 | Schedule 10 | 40 | 11.78 | 471.2
|  |  |  | Sub total | 954.83
|  |  |  | Wp(incld 15%) | 1098.0545
| Total weight considering zone influence |  |  | Fpw=Cp*Wp | 768.6381
Note: Fpw should be smaller than maxum load of pipe on Table 9.3.5..3.2
|  |  |  | Maxium load Fpw | 1900 | from table 9.3.5.3.2
| Fastner load | 1200 | from Table 9.3.5.9.1
| Brace attachment | 1744.5887 | from Table 9.3.5.8.7(a)
Brace